# Water Supply National Engineering Design Standards

# Working Draft version 1 – August 2023

Work to develop a technical code for drinking, waste and stormwater infrastructure has been known as the Code of Practice. This name is now changing to the National Engineering Design Standards. This name is more reflective of The Water Services Entities Amendment Bill, which requires Water Services Entities to have a development code. A subset of the development code requires entities to ensure they specify applicable engineering design standards to water infrastructure.

Water Supply National Engineering 
Design Standards

| Revision | Date | Details | Author | Checked | Approved |
| --- | --- | --- | --- | --- | --- |
| Working Draft | 25 August 23 | Issue 1, v1.0 | TWG | SJ | NSG |

TWG Water Sub Group:

Kelly Nikora, Eugene Kroukam, Evan Vaughters, Andrew Pascoe, Michael Galambos

Table of Contents

FRONTMATTER	1

FOREWORD	1

National Engineering Design Standards Development	1

Acknowledgements	1

Publication History	2

Disclaimer	2

Copyright	2

INTRODUCTION	3

The Need for a National Engineering Design Standard	3

The Benefits of National Engineering Design Standards	3

Purpose	3

Scope	3

Requirements and Informative NEDS	4

Te Mana o te Wai	4

Water Services Entities Amendment Bill	5

ADDITIONAL CONSIDERATIONS	6

Safety in Design (SiD)	6

Technical and guideline publications	6

Products and Material Information and Guidance	6

Approach to Innovation	7

Natural Hazards	7

NEDS Approach to Climate Change	7

NEDS Approach to Sustainability	8

APPENDICES	9

GLOSSARY, ABBREVIATIONS AND REFERENCES	10

GLOSSARY OF TERMS	10

ABBREVIATIONS	12

REFERENCED DOCUMENTS	13

PART ONE - PLANNING AND DESIGN	15

1	GENERAL	16

1.1	SCOPE	16

1.2	PLANNING AND DESIGN	16

1.2.1	Scope and requirements	16

1.2.2	Concept Design Statement	17

1.2.3	Detailed design	17

1.2.4	Design life	18

1.2.5	Carbon Reduction	18

2	SYSTEM PLANNING	19

2.1	GENERAL	19

2.1.1	Structure plan/Infrastructure Master Plan	19

2.1.2	Future development	19

2.2	SYSTEM CONFIGURATION	19

2.2.1	Point of Supply	19

2.3	SYSTEM PLANNING PROCESS	20

2.3.1	General	20

2.3.2	Extending / upgrading an existing water supply system	20

2.3.3	Providing a new water supply	21

2.3.4	Non-drinking water as drinking water substitution	21

2.4	DEMANDS	21

2.4.1	General	21

2.4.2	Dual water supply systems	21

2.4.3	Demand assessment	22

2.4.4	Peak demands	25

2.5	SYSTEM HYDRAULICS	26

2.5.1	General	26

2.5.2	Network analysis	26

2.5.3	Operating pressures	26

2.5.4	Pressure variation analysis	28

2.5.5	Determining supply zones	28

2.6	WATER QUALITY	29

2.6.1	General	29

2.6.2	Prevention of Backflow	29

2.6.3	Water age	30

2.6.4	Disinfection	30

2.7	PUMPING STATIONS	31

2.8	SERVICE RESERVOIRS	31

2.9	TRENCHLESS TECHNIQUES FOR PIPELAYING	31

2.10	FUTURE SYSTEM EXPANSION	31

2.11	SYSTEM REVIEW	31

3	HYDRAULIC DESIGN	31

3.1	SIZING	31

3.1.1	General	31

3.1.2	Minimum pipe sizes	32

3.1.3	Empirical sizing of reticulation mains	32

3.1.4	Fire flows	33

3.1.5	Sizing by analysis	33

3.2	DESIGN PRESSURES	34

3.3	PRESSURE CLASS OF SYSTEM COMPONENTS	35

3.3.1	Reticulation systems	35

3.3.2	Systems subjected to dynamic pressures	35

3.4	THRUST AND ANCHOR BLOCK DESIGN	35

3.5	SYSTEM TEST PRESSURE	35

3.6	DESIGN FOR DYNAMIC STRESSES	35

3.6.1	Fatigue	35

3.7	TEMPERATURE DE-RATING OF PLASTICS PIPES AND FITTINGS	36

3.8	DE-RATING OF MANUFACTURED PE COMPONENTS	37

4	PRODUCTS AND MATERIALS	37

4.1	GENERAL	37

4.1.1	Pipe selection	37

4.1.2	Standard pipe sizes	37

4.1.3	Minimum pipe sizes	38

4.1.4	Pipe PN class (pressure rating)	38

4.1.5	Design pressure	38

4.1.6	Minimum pipe PN	38

4.1.7	Nominated pipe PN	38

4.1.8	Pumped mains	38

4.1.9	Pipe materials	39

4.1.10	Steel mains considerations	39

4.2	PROTECTION AGAINST DEGRADATION	39

4.2.1	Protection against contaminated ground	39

4.2.2	Bolted connections	39

5	GENERAL DESIGN	39

5.1	GENERAL REQUIREMENTS	39

5.1.1	Design tolerances	39

5.1.2	Levels	40

5.1.3	Water main renewals electrical safety and earthing to water services	40

5.1.4	Survey Control	40

5.2	RETICULATION DESIGN FOR WATER QUALITY	40

5.2.1	Layout of water mains	40

5.2.2	Looped mains	41

5.2.3	Link mains	41

5.2.4	Reduced size mains	41

5.3	WATER MAIN ACCESS	41

5.4	LOCATION OF WATER MAINS	41

5.4.1	General	41

5.4.2	Water mains in road reserves	42

5.4.3	Location in other than dedicated public road reserves	42

5.4.4	Effect on vegetation	42

5.4.5	Water mains near trees	43

5.4.6	Contaminated sites	43

5.4.7	Safety in Design	44

5.4.8	Location markers	44

5.4.9	Marking tape	44

5.5	CROSSINGS	45

5.5.1	Location of water mains on bridges	45

5.5.2	Crossings	45

5.6	VALVES	46

5.6.1	Valves	46

5.6.2	Valving design	46

5.6.3	Pressure reducing valves (PRV)	48

5.6.4	Pressure relief valves (PRelV)	48

5.6.5	Pump control valves	49

5.6.6	Pressure sustaining valves (PSV)	49

5.6.7	Air valves (AV)	49

5.6.8	NON-RETURN VALVES	49

5.6.9	SCOURS AND PUMP-OUT BRANCHES	50

5.7	SWABBING POINTS	51

5.8	HYDRANTS	51

5.8.1	Purposes	51

5.8.2	Hydrant siting principles	51

5.9	DISINFECTION FACILITIES	52

5.9.1	General	52

5.10	TRENCHLESS TECHNOLOGY	52

5.11	SHARED TRENCHING	53

5.12	RIDER MAINS	53

5.12.1	Principal and rider mains layout	53

5.12.2	Rider mains and duplicate principal mains	53

5.13	CONNECTION OF NEW MAINS TO EXISTING MAINS	53

5.13.1	General	53

5.14	TERMINATION POINTS	54

5.14.1	Permanent ends of water mains	54

5.14.2	Temporary ends of water mains	55

5.14.3	Flushing points	56

5.15	PROPERTY SERVICES	56

5.15.1	General	56

5.15.2	Multiple Dwellings	57

5.15.3	Service line connections	57

5.16	OBSTRUCTIONS AND CLEARANCES	58

5.16.1	Clearance from structures and property boundaries	58

5.16.2	Underground obstructions and services	59

5.16.3	Clearance from transmission towers	61

5.16.4	Deviation of water mains	61

6	SYSTEM PRESSURE MANAGEMENT	62

6.1	GENERAL	62

6.2	IN-LINE PRESSURE BOOSTER PUMPING STATIONS	62

6.3	PRESSURE REDUCING VALVE INSTALLATIONS	62

6.4	PRESSURE SUSTAINING VALVE INSTALLATIONS	63

7	STRUCTURAL DESIGN	63

7.1	GENERAL	63

7.2	STRUCTURAL CONSIDERATIONS	63

7.3	INTERNAL FORCES	63

7.4	EXTERNAL FORCES	63

7.4.1	General	63

7.4.2	Pipe cover	63

7.4.3	Embedment zone dimensions	64

7.4.4	Pipe embedment	64

7.4.5	Buoyancy	64

7.5	GEOTECHNICAL CONSIDERATIONS	64

7.5.1	General	64

7.5.2	Water mains in engineered or controlled fill	65

7.5.3	Water mains in non-engineered fill	65

7.5.4	Construction of an embankment	65

7.6	CONCRETE ENCASEMENT	66

7.6.1	General	66

7.6.2	Encased steel pipelines	66

7.7	WATER MAINS IN UNSTABLE GROUND	66

7.8	ABOVE-GROUND WATER MAINS	67

7.9	PIPELINE ANCHORAGE	67

7.9.1	General	67

7.9.2	Thrust blocks	67

7.9.3	Anchor blocks	67

7.9.4	Restrained elastomeric seal joint water mains	67

7.9.5	Restraint requirements for special situations	68

7.10	BULKHEADS AND TRENCHSTOPS	68

7.11	UNFORESEEN GROUND CONDITIONS	68

7.12	SEISMIC DESIGN	69

7.12.1	General	69

7.12.2	Buried Linear Assets	70

7.12.3	Above Ground and Non-Linear Structures	71

7.12.4	Connections Between Structures and Buried Assets	72

8	DESIGN REVIEW AND DRAWINGS	72

8.1	DESIGN REVIEW	72

8.2	DESIGN DRAWINGS	72

8.2.1	General	73

8.2.2	Composition of Design Drawings	73

8.2.3	Scale	73

8.2.4	Contents of Design Drawings	73

8.2.5	Pipeline system acronyms	73

8.3	SPECIFICATIONS	73

8.4	RECORDING OF WORK AS CONSTRUCTED INFORMATION	73

PART TWO – CONSTRUCTION	75

9	GENERAL	76

9.1	SCOPE	76

9.2	HEALTH AND SAFETY	76

10	GENERAL CONSTRUCTION	76

10.1	GENERAL	76

10.2	ORDER OF CONSTRUCTION, TESTING AND COMMISSIONING	77

10.3	CUSTOMER FOCUS	77

10.3.1	General	77

10.3.2	Resolution of complaints	77

10.4	PROTECTION OF PROPERTY AND ENVIRONMENT	77

10.4.1	Protection of other services	78

10.4.2	Road reserves or other thoroughfares	79

10.4.3	Private and public lands	79

10.4.4	Protection of the environment and heritage areas	80

10.5	DISUSED WATER, WASTEWATER AND STORMWATER PIPES	80

10.6	OPERATION OF WATER SUPPLY NETWORK	81

10.7	CONCRETE WORKS	82

10.8	SUPPLY OF WATER TO THE WORKS	82

10.9	SUPPLY OF WATER TO EXISTING PROPERTIES	82

10.10	ALTERATION OF EXISTING SERVICES	82

10.11	SURVEY MARKS	82

10.12	LATENT CONDITIONS	82

10.13	SERVICE CONFLICTS	82

10.13.1	Abandoned Services	82

10.13.2	Live Laterals Fouled by the Proposed Pipeline	83

10.13.3	Unavoidable Diversion of Services	83

10.13.4	Clearance to Other Services	83

10.13.5	Separation from Structures	83

11	PRODUCTS AND MATERIALS	84

11.1	AUTHORISED PRODUCTS AND MATERIALS	84

11.1.1	General	84

11.2	DELIVERY INSPECTION OF PRODUCTS AND MATERIALS	84

11.3	TRANSPORTATION, HANDLING AND STORAGE OF PRODUCTS AND MATERIALS	85

11.3.1	General	85

11.3.2	Transportation	85

11.3.3	Unloading and handling	85

11.3.4	On-site storage	85

11.4	REJECTED PRODUCTS AND MATERIALS	86

12	EXCAVATION	86

12.1	EARTHWORKS GENERAL	86

12.2	PRECAUTIONS	86

12.3	LIMITS OF CLEARING AND EXCAVATION	87

12.3.1	Topsoil stripping	87

12.3.2	Stockpiling	87

12.4	Health & Safety During Earthworks	87

12.5	PROTECTION OF TREES	88

12.5.1	General precautions	88

12.5.2	Protection of roots	88

12.6	BLASTING	88

12.7	SUPPORT OF EXCAVATIONS	89

12.8	DRAINAGE AND DEWATERING	89

12.9	EXCAVATION ACROSS IMPROVED SURFACES	89

12.10	TRENCH EXCAVATION	90

12.10.1	General	90

12.10.2	Construction of embankment	90

12.10.3	Clearances for on-site works	90

12.11	REFILL OF EXCESSIVE EXCAVATION	90

12.12	FOUNDATIONS AND FOUNDATION STABILISATION	90

12.13	SURPLUS EXCAVATED MATERIAL	91

13	BEDDING FOR PIPES	91

13.1	TRENCH FLOOR PREPARATION	91

13.2	BEDDING AND PIPE SUPPORT	91

13.3	SPECIAL PIPE SUPPORT FOR NON-SUPPORTIVE SOILS	92

14	PIPE LAYING, JOINTING AND CONNECTING	92

14.1	INSTALLATION OF PIPES	92

14.1.1	General	92

14.1.2	Cleaning, inspection, and joint preparation	93

14.1.3	Laying	93

14.1.4	Lift and re-lay construction	94

14.2	HORIZONTAL AND VERTICAL DEFLECTIONS OF PIPES	94

14.2.1	General	94

14.2.2	Deflection at a pipe joint	94

14.2.3	Curving of pipe	94

14.3	HORIZONTAL AND VERTICAL SEPARATION OF CROSSING PIPELINES	94

14.4	VALVES, HYDRANTS AND OTHER APPURTENANCES	94

14.5	UNDER PRESSURE CUT-IN CONNECTION TO PRESSURE PIPES ≥DN 80	95

14.5.1	Inspection of host pipe	95

14.5.2	Inspection of valve to be installed	95

14.5.3	Disinfection of fittings and equipment	95

14.5.4	Installation of off-take clamp	95

14.5.5	Installation of the valve	96

14.5.6	Cut-in operation	96

14.5.7	Recording and reporting	96

14.6	FLOTATION CONTROL	96

14.7	THRUST AND ANCHOR BLOCKS AND RESTRAINED JOINTS	97

14.8	TAPPING OF MAINS, PROPERTY SERVICES AND WATER METERS	97

14.9	TRENCH STOPS	98

14.10	BULKHEADS	98

14.11	CORROSION PROTECTION OF DUCTILE IRON	99

14.12	MARKING TAPES	99

14.12.1	Detectable marking tape	99

14.12.2	Tracer wire	99

14.13	VALVES, HYDRANTS AND SURFACE BOXES AND FITTINGS	99

14.13.1	Installation	99

14.14	PIPES IN DUCTS UNDER ROADS, RAILWAYS AND ELSEWHERE	100

14.15	BRIDGE CROSSINGS	101

14.16	APPURTENANCE LOCATION MARKING	101

14.17	FLANGED JOINTS	101

14.18	WELDING OF STEEL PIPELINES	101

14.18.1	General	101

14.18.2	Field welding of flanges	101

14.18.3	Reinstatement of cement mortar lining	102

14.18.4	Reinstatement of external corrosion protection at joints using a heat-shrinkable sleeve system	103

14.19	WELDING OF PE PIPELINES	103

14.19.1	General	103

14.19.2	Welder qualifications	104

14.19.3	Connections to pipes of other materials	104

14.19.4	Thermoplastic jointing of Polyethylene by electrofusion welding	104

14.19.5	Site butt fusion welding of Polyethylene pipe and fittings	106

14.19.6	Polyethylene Pipe Weld Test	109

15	PIPE EMBEDMENT AND SUPPORT	112

15.1	GENERAL	112

15.2	EMBEDMENT MATERIALS	113

15.2.1	General	113

15.2.2	Recycled, reused and waste materials	113

15.3	COMPACTION OF EMBEDMENT	113

15.3.1	Methods	113

15.3.2	Compaction trials / Pre-qualification of embedment compaction method	114

15.3.3	Compaction control	114

15.3.4	Surplus material	114

15.4	SPECIAL BEDDING AND EMBEDMENTS / GEOTEXTILE SURROUND AND PILLOW	116

15.5	REMOVAL OF TRENCH SUPPORTS	116

15.6	CONCRETE EMBEDMENT AND ENCASEMENT	116

16	TRENCHLESS INSTALLLATION FOR BORED PIPES UNDER ROADS, DRIVEWAYS AND ELSEWHERE	116

16.1	GENERAL	116

16.2	HORIZONTAL DIRECTIONAL DRILLING (HDD)	116

16.2.1	Calculations	117

16.2.2	Construction plan	117

16.2.3	Tracking systems	118

16.2.4	Drilling fluids and cuttings management plan	118

16.2.5	Contingency plans	118

16.2.6	Grouting	118

16.2.7	Record keeping	118

17	FILL	121

17.1	BACKFILL AND FILL IN GENERAL	121

17.2	GENERAL COMPACTION OF BACKFILL	121

17.3	BACKFILL MATERIAL CLASSIFICATION	121

17.4	TRENCH FILL	122

17.4.1	General	122

17.4.2	Material requirements	122

17.5	EMBANKMENT FILL	122

17.6	DRIVES AND TUNNEL FILL	123

17.7	HAUNCHING AND BACKFILL	123

17.7.1	Difficult ground conditions	123

17.7.2	Scour	124

18	SWABBING	124

18.1	GENERAL	124

18.1.1	Cleaning	124

18.1.2	Disinfection by chlorination	124

18.2	SWABS	124

18.2.1	SWABBING PROCEDURE	124

19	ACCEPTANCE TESTING	125

19.1	GENERAL	125

19.2	VISUAL INSPECTION	125

19.3	COMPACTION TESTING	126

19.3.1	General	126

19.3.2	Embedment compaction testing	127

19.3.3	Trench fill compaction testing	127

19.3.4	Other fill compaction testing	128

19.4	HYDROSTATIC PRESSURE TESTING	128

19.4.1	General	128

19.4.2	Hydrostatic test	128

19.4.3	Hydrostatic test procedure	128

19.4.4	Pressure pipelines general requirements – Field hydrostatic pressure testing	129

19.4.5	Selection of test pressure	129

19.4.6	Selecting test lengths	129

19.4.7	Pre-test procedures	130

19.4.8	Post-test procedures	131

19.4.9	Constant pressure test (water loss method) – PVC, DI, GRP, and steel pipelines	132

19.4.10	Pressure decay test for PE pipe larger than DN200 or longer than 250m	133

19.4.11	Pressure rebound test for PE up to DN 200	134

19.4.12	Visual test for small pressure pipelines	135

19.4.13	Hydrostatic pressure test for PE pressure pipelines	135

20	DISINFECTION	135

20.1	APPLICATION	135

20.2	CLEANING	136

20.3	DISINFECTION BY CHLORINATION	137

20.3.1	Testing	137

20.4	DISINFECTION PROCEDURE FOR WATERMAINS TO BE CAPPED AND PUT INTO SERVICE IN THE FUTURE	138

20.5	FLUSHING OF DISINFECTION WATER	138

21	TOLERANCES ON AS-CONSTRUCTED WORK	139

21.1	GENERAL	139

21.2	HORIZONTAL TOLERANCES	139

21.2.1	Water mains and in-line structures	139

21.2.2	Property services and meters	139

21.3	VERTICAL TOLERANCES	140

21.3.1	Water mains, property connections and structures	140

21.3.2	Verticality ("plumb")	140

21.4	TOLERANCES ON FINISHED SURFACE STRUCTURES AND FITTINGS	140

21.5	CAST IN-SITU CONCRETE STRUCTURES AND SLABS	140

22	CONNECTIONS TO EXISTING WATER MAINS	140

22.1	GENERAL	140

22.1.1	UNDER PRESSURE CONNECTIONS	141

22.2	INSERTED TEE CONNECTIONS	141

22.2.1	Shutdown of existing water mains	141

22.2.2	Making the connection to existing water main	141

22.2.3	Re-charging the shutdown water main	142

22.3	CONNECTION AND/OR CHARGING THE NEW WATER MAINS	142

22.4	RECONNECTION OF PROPERTIES SUPPLIED BY TEMPORARY PRIVATE SERVICES	142

23	RESTORATION	142

23.1	GENERAL	142

23.2	PAVEMENTS	143

23.3	LAWNS	143

23.4	GRASSED AREAS	143

23.5	PROVISION FOR AND RECTIFICATION OF SETTLEMENT	144

23.6	MAINTENANCE OF RESTORED SURFACES	144

24	WORK AS CONSTRUCTED DETAILS	144

Appendices	145

Appendix A - Water Standard Drawings	146

Appendix B - Water Design Guide Matrix	167

Appendix C - Safety in Design Risk Register	168

Appendix D - Omissions & Opportunities Register	169

Appendix E – Concrete Construction Checklist	170

Appendix F - General Requirements for Site Butt Fusion Jointing	171

Appendix G - Electrofusion Welding Check Sheet	172

Appendix H - Compliance Requirement Check Sheet	173

Appendix I - Pipe Butt Weld Record Log Sheet	174

Appendix J - Pipe Electrofusion Weld Record Log Sheet	175

Appendix K - PE Weld testing Information Requirements	176

GLOSSARY, ABBREVIATIONS AND REFERENCES

GLOSSARY OF TERMS

| Table 1-1 - Glossary |  |
| --- | --- |
| Glossary |  |  |
| BPD | Backflow Prevention Device |  |
| Backflow | The unwanted reverse flow of water in a drinking water system, potentially carrying pollutants or contaminants, and is defined in the Water Services Act 2021 as ‘the unplanned reversal of flow of water or mixtures of water and contaminants into the water supply system’. |  |
| BFP | Backflow Prevention |  |
| Backflow prevention assembly (BFPA) | The complete valve train compiled from the water suppliers Approved Product Register - upstream isolation valve, strainer, BFP device, downstream isolation valve. A water meter may be included in this assembly, if required by the water supplier. |  |
| Cross-connection | As defined in AS/NZS 3500.0 Definitions as any connection or arrangement, physical or otherwise, between any drinking water supply system either directly or indirectly connected to a water main, and any fixture, storage tank, receptacle, equipment or device through which it may be possible for any non-drinking water, used, unclean, polluted or contaminated water, or any other substance, to enter any part of such drinking water system under any conditions. |  |
| BSP | Bulk Supply Point |  |
| CAR | Corridor Access Request |  |
| CCTV | Closed Circuit Television |  |
| Charging [the watermain] | Filling the watermain with potable water from the Entity’s supply network |  |
| Chlorination | Increasing the concentration of free available chlorine to achieve disinfection over a 24-hour period. Concentration range of 5-10ppm |  |
| DWSNZ | Drinking Water Standards for New Zealand referencing Water Services (Drinking Water Standards for New Zealand) Regulations 2022 |  |
| ESF | Engineering Standards Framework |  |
| FAC | Free Available Chlorine or Chlorine Residual |  |
| HSNO Act | Hazardous Substances and New Organisms Act 1996 and associated regulations |  |
| IQP | Independent Qualified Person - a person approved by a territorial authority as qualified to inspect a specified building system and ensure that necessary maintenance occurs (under the Building Warrant of Fitness process). “Independent” means they have no financial interest in the building. This is defined in Section 7 of the Building Act 2004. |  |
| kPa | Kilo Pascal |  |
| Local Network / Reticulation | The reticulated distribution system from the transmission system to the point of supply to the customer (the water meter), less than 300mm in diameter |  |
| L or l | Litre |  |
| L/s | Litres per second |  |
| m | Metre |  |
| mg/L | Milligrams per litre (equivalent to ppm) |  |
| mL | Millilitres |  |
| MPN | Most Probable Number |  |
| Plumber | A plumber is trained, assessed and qualified to either a Licenced or Certified level, then authorised to practice by the Plumbers, Gasfitters and Drainlayers Board to the Plumbers, Gasfitters and Drainlayers Act 2006. |  |
| PPE | Personal Protective Equipment |  |
| ppm | Parts per million (equivalent to mg/L) |  |
| SDS | Safety Data Sheet |  |
| Superchlorination | Increasing the concentration of free available chlorine (FAC) to achieve disinfection over a 1-hour period. Concentration of FAC will be at 80-100ppm |  |
| SiD | Safety in Design |  |
| Transmission Network | The bulk distribution system from water treatment plants to reservoir storage and/or bulk supply points. Transmission mains can be differentiated from Local Networks mains in that customer connections are generally only on Local Networks mains, and they are >300mm in diameter. There may be some exceptions, in which case the Entity should be contacted for clarification. |  |
| Water Supply System | The combined transmission and local network drinking water supply system |  |
| WTPs | Water Treatment Plants |  |
| Annual exceedance probability (AEP) | The probability of exceedance of a given occurrence, generally a storm, in a period of 1 year (1% AEP is equal to 1 in 100 year storm). |  |
| Assets | Water, wastewater, and stormwater infrastructure owned and operated by a water service entity WSE. |  |
| Brownfield | A land area that has existing or legacy infrastructure, or land that has been contaminated. |  |
| Developer | An individual or organisation having the financial responsibility for the development project. Developer includes the owner. |  |
| Designer | The developer’s professional advisor, appointed by the developer to complete the investigation, design, contract administration, construction supervision, and certification of the works on completion. |  |
| Dwelling | Any building or group of buildings, or part thereof used, or intended to be used principally for residential purposes and occupied or intended to be occupied by not more than one household. |  |
| Dwelling unit equivalent (DUE) | A unit of water demand of 220 kilolitres per year on average, or, where a wastewater meter is installed, a unit of wastewater discharge of 209 kilolitres per year on average. The number of DUE’s is based on the additional demand for water and/or wastewater at the property and will be rounded to the nearest whole number. |  |
| Greenfield | A land area that has no prior infrastructure development and is not contaminated. |  |
| Infill | Development within a previously developed area. |  |
| Local water network | The reticulated distribution system from the water transmission systems to each property. Pipelines are generally less than DN300. |  |
| Water transmission | The water transmission system covers the bulk conveyance of water to reservoir storage or to bulk supply points. Customers are not supplied directly from transmission systems. |  |
| Peet valve | A gate valve that is installed on a rider main, sometimes referred to as an isolation valve |  |
| Point of supply | The ‘point of supply’ is the point where the public network connects with a private network. At this point, the responsibility for ownership and maintenance of assets and equipment transfers from a WSE to the customer. |  |
| Drinking Water | Term used in the Water Services Act 2021 to denote potable water. |  |
| Private connection | Private connection is the pipe connection from the private property up to the point of connection, usually a meter box. |  |
| Principal main | A watermain that is DN100 or greater. Fire hydrants may be installed on a principal main. |  |
| Rider main | A water supply main that is supplied from a principal watermain. A rider main is smaller than the principal main, but not less than DN50. |  |
| Service lead | The lateral pipe connection up to the point of supply is installed in public road reserve and is owned by the WSE. The service lead is also commonly referred to as the “service connection” or “lateral connection” |  |
| Structure | A piece of infrastructure (excluding pipework), that may be constructed from various types of materials that includes something built or arranged such as underground chambers or pits, a building or building components such as foundations, piles or retaining walls. |  |
| Sluice valve | A gate valve used for sluicing or scouring debris from a water main. |  |
| System (water/network/ reticulation) | The interconnected hydrological engineered layout of hydraulic components such as pipes, valves and pumps. |  |
| Toby Valve | A small isolation valve <DN50 installed on a service lead. Referred to as a Toby in the Water Services Act 2021. |  |

ABBREVIATIONS

| Table 1-2 – Abbreviations |  |
| --- | --- |
| Abbreviations |  |
| AEP | Annual exceedance probability |
| CBD | Central business district |
| CCO | Council controlled organisation |
| CoP | Code of Practice |
| CLS | Concrete lined steel (pipe) |
| DN | Nominal diameter |
| EPDM | ethylene propylene diene monomer rubber |
| ESF | Engineering standards framework |
| FENZ | Fire and Emergency New Zealand |
| ha | hectare |
| L/d | Litres per day |
| L/p/d | Litres per person per day |
| L/m²/d | Litres per square metre area per day |
| L/s | Litres per second |
| HGL | Hydraulic grade level |
| H&S | Heath and Safety |
| IQP | Independent qualified person |
| m | metre |
| m2 | square metre (area) |
| mm | millimetres |
| MPa | megapascal |
| m/s | metres per second |
| NB | Nominal bore. The inside diameter of a pipe |
| NEDS | National Engineering Design Standards |
| NPS-FM | National Policy Statement Freshwater Management |
| OD | Outside diameter |
| PE | Polyethylene |
| PF | Peaking factor |
| PN | Pressure nominal. Maximum rated operating pressure |
| PE 100 | Polyethylene with MRS=10MPa |
| PE 80 | Polyethylene with MRS = 8MPa |
| PVC-U | Unplasticised PVC |
| PVC-M | Modified PVC |
| PVC-O | Orientated PVC |
| PP | Polypropylene |
| PB | Polybutylene |
| ABS | Acrylonitrile Butadiene Styrene |
| PE-X | Cross-linked Polyethylene |
| PTFE | Polytetrafluorethylene |
| RPZD | Reduced Pressure Zone Device used for backflow prevention in some circumstances |
| SBR | Styrene-butadiene rubber |
| NBR | Nitrile-butadiene rubber |
| WSE | Water Services Entity |

REFERENCED DOCUMENTS

RELEVANT LEGISLATION, REGULATIONS AND STANDARDS:

Resource Management Act (RMA, 1991)

District Plans

Regional Plans

Water Services Act 2021

Water Services Entities Act 2022

Water Services Entities Amendment Act 2023

Water Services Legislation Act 2023

Drinking Water Quality Assurance Rules 2022

Building Act 2004

Building Code (Schedule 1 of the Building Regulations 1992)

Building Code Acceptable Solutions and Verification Methods

Health and Safety at Work Act 2015

Hazardous Substances and New Organisms Act 1996 and associated regulations (HSNO)

Data Quality / Quality of Work/ Electronic Data / As Built Plans

AS5488-2013 AS 5488-2013 Subsurface Utility Engineering (S.U.E.)

Earthworks and roading

NZS 4404:2010. Land development and subdivision infrastructure
NZS4402 Methods of testing soils for civil engineering purposes
AS 1289.6.9.1 Methods for testing soils for engineering purposes – Soil strength and consolidation test – Determination of stiffness of soil – Clegg impact value
Approved Code of Practice HSNOCOP 55 Storage of Explosives
BS 5930 Code of Practice for ground investigations
NZTA F2 (New Zealand Transport Agency) – Specification for pipe subsoil drain construction
TNZ B/02 (New Zealand Transport Agency) – Specification for construction of unbound granular pavement layers
NZTA M1 (New Zealand Transport Agency) – Specification for roading bitumens
NZTA M10 (New Zealand Transport Agency) – Specification for dense graded and stone mastic asphalts

Pipe and duct laying

AS/NZS 2566 Buried flexible pipelines, Part 1: Structural design

AS/NZS 2566 Buried flexible pipelines, Part 2: Installation
AS/NZS 2032 Installation of PVC pipe systems
AS/NZS 2033 Installation of polyethylene pipe systems
AS/NZS 4130 Polyethylene (PE) pipes for pressure applications
POP001 Electrofusion jointing of PE pipes and fittings for pressure applications
POP003 Butt fusion jointing of PE pipes and fittings – recommended parameters
POP005 Packaging, handling and storage of polyethylene pipes and fittings
AWWA C209 Cold-applied tape coatings for steel water pipe, special sections, connections and fittings

Pipe and Fittings Standards

AS/NZS 1254:2010 PVC-U pipes and fittings for stormwater and surface water applications

AS/NZS 1260:2009 PVC-U pipes and fittings for drain, waste and vent application

AS/NZS 1477:2006 PVC pipes and fittings for pressure applications

AS/NZS 2032:2006 Installation of PVC pipe systems

AS/NZS 2033:2023 Installation of polyethylene pipe systems

AS/NZS 2041:1998 Buried corrugated metal structures

AS/NZS 2280:2004 Ductile iron pipes and fittings

AS/NZS 4441:2017 Oriented PVC (PVC-O) pipes for pressure applications

AS/NZS 4765:2017 Modified PVC (PVC-M) pipes for pressure applications

AS/NZS 5065:2005 Polyethylene and polypropylene pipes and fittings for drainage and sewerage applications

AS/NZS 4020:2005 Testing of products for use in contact with drinking water

AS/NZS 4058:2007 Precast concrete pipes (pressure and non-pressure)

AS/NZS 4087:2011 Metallic flanges for water works purposes

AS/NZS 4129:2008 Fittings for polyethylene (PE) pipes for pressure applications

AS/NZS 4130:2018 Polyethylene (PE) pipes for pressure applications

AS/NZS 4131:2010Polyethylene (PE) compounds for pressure pipes and fittings

AS/NZS 4158:2003 Thermal-bonded polymeric coatings on valves and fittings for water industry purposes

AS/NZS 4793:2009 Mechanical tapping bands for waterworks purposes

AS/NZS 4998:2009 Bolted unrestrained mechanical couplings for waterworks purposes

AS/NZS 5065:2005 Polyethylene and polypropylene pipes and fittings for drainage and sewerage applications

Trenchless Pipe Installation

ISO 21225.1 Plastics Piping Systems for the trenchless replacement of underground networks

Replacement on the line by pipe bursting and pipe extraction

ISO 21225.2 Plastics Piping Systems for the trenchless replacement of underground networks

Replacement off the line by horizontal direction drilling and impact moling

Trenchless Renovation Techniques using PE Pipes

(ISO 11296 series)

Non-pressure drainage and sewerage networks

(ISO 11297 series)

Drainage and sewerage networks under pressure

(ISO 11298 series)

Water supply networks

ISO 11298 Plastic piping systems for renovation of underground water supply systems
Part 1 – General
Part 2 – Lining with continuous pipes
Part 3 – Lining with close fit pipes

AS 2200-2006 Design charts for water supply and sewerage

AS/NZS 1516 The cement mortar lining of pipes in-situ
AS 1012 part 24 Methods of testing concrete – Determination of the tensile bond strength of concrete – Repairs and strengthening systems

Concrete

AS/NZS 1554 part 3 Welding of reinforcing steel

NZS 3104 Specification for concrete production

NZS 3109 Concrete construction

NZS 3111 Methods of test for water and aggregate for concrete

NZS 3112 Methods of test for concrete

Part 1 Tests relating to fresh concrete

Part 2 Tests relating to the determination of strength of concrete

Part 3 Tests on hardened concrete other than strength
Part 4 Tests relating to grout
AS/NZS 1170:2004 – Structural Design Actions

NZS 3106:2009 – Design of Concrete Structures for the Storage of Liquids

NZS 3114 Specification for concrete surface finishes
NZS 3121 Specification for water and aggregate for concrete
NZS 3152 Specification for the manufacture and use of structural and insulating lightweight concrete
NZS 4219:2009 – Seismic Performance of Engineering Systems in Buildings

AS/NZS 4671 Steel reinforcing materials
AS/NZS 4672 part 1 and part 2 Steel pre-stressing materials
AS/NZS 3679 part 1 Structural steel – Hot-rolled bars and sections

Formwork and temporary works

AS 3610 Formwork for concrete
AS/NZS 4994.4 Temporary edge protection – Part 4 Perimeter protection screens
AS/NZS 5131 Structural steelwork – Fabrication and Erection Painting
BS5252 Framework for colour co-ordination for building purposes
ASTM D-610-08 Method of evaluating degree of rusting on painted steel surfaces
AS/NZS 2311 Guide to the painting of buildings
AS/NZS 2312 part 1 Guidelines for the protection of iron and steel against exterior atmospheric corrosion
Steel Structures Painting Council (SSPC) Painting manual
Volume 1: Good painting practice
Volume 2: Systems and specifications

Demolition

AS2601 Demolition of structures

Masonry

NZS 4210 Masonry construction: materials and workmanship
AS 1316 Masonry cement
AS/NZS 2699 part 1 and 2 Built-in components for masonry construction
AS/NZS 2904 Damp-proof courses and flashings
Building Code Schedule 1 of the Building Regulations 1992

Plumbing and Network Reticulation

AS/NZS 2845 Water Supply – Backflow prevention devices

Part 1: 2022 Materials, design and performance requirements

Part 2: 2010 Water supply - Backflow prevention devices, registered air gaps and registered break tanks

Part 3: 2020 Field testing and maintenance of testable devices

BS EN 12502-3 Galvanised coatings
NZS/BS 1387 Steel tubes for threading to BS21 pipe threads
New Zealand Building Code G12/AS1 (Water Supplies Acceptable Solution)

AS/NZS 3500.0:2021 Plumbing and drainage, Part 0: Glossary of terms

AS/NZS 3500.1:2021 Plumbing & drainage, Part 1: Water services

ASSE 1060:2017 Performance requirements for outdoor enclosures for fluid conveying components.

AS/NZS 4020:2018 Testing of products for use in contact with drinking water

Electrical

AS/NZS 3000: 2018 Electrical installations – known as the Australian/New Zealand Wiring Rules

AS/NZS 4853: 2012 Electrical hazards on metallic pipelines

Fire Fighting

SNZ PAS 4509:2008 New Zealand Fire Service Firefighting Water Supplies Code of Practice

PART ONE - PLANNING AND DESIGN

# GENERAL

This volume sets out requirements for the planning and design of water networks for network renewals, upgrades, land development, and subdivision. It also guides the assessment and upgrade of existing water systems to service brownfield and infill developments. It covers the design of water pipes for the purpose of supplying water for drinking, including restricted flow supply, and firefighting purposes up to and including 300mm diameter. All trunk mains, booster pump stations, reservoirs and pressure management devices will require specific design in conjunction with the WSE and are excluded.

Where investigations and reports are required by a suitably qualified person, this person or persons will have nationally recognised qualifications and accreditation, such as Chartered Professional Engineer (CPEng), Certified Professional Land Development Engineer or Certified Professional Engineering Surveyor.

The person or persons will normally be expected to be professionally recognised in the area of competence claimed and to carry professional indemnity insurance to a level suitable for the purpose.

The Water Services Entity (WSE) reserves the right to have any work peer reviewed regardless of any prior approval as to the acceptability of the suitably qualified person. The cost of all peer review work will be borne by the developer as referenced in the WSE Development Code.

Without limiting the Entity’s rights to require the use of suitably qualified persons the following are examples of areas of expertise, together with the expected minimum qualifications where such people may be required:

Potable water supply engineering (CPEng with recognised Water engineering discipline competence);

Geotechnical engineering (CPEng with recognised discipline competence);

Traffic and transportation engineering (CPEng with recognised discipline competence);

Landscape design and practice (Registered Landscape Architect);

Land surveyor (subdivision plans and Land legalisation) (Certified Professional Land Development Engineer (CPLDEng) or a Certified Professional Engineering Surveyor (CPESurv))

Fire Engineering (CPEng with recognised discipline completence)

## SCOPE

This NEDS covers the design of water pipes for the purpose of supplying water for drinking, including restricted flow supply, and firefighting purposes up to and including 300mm diameter. All trunk mains, booster pump stations, reservoirs and pressure management devices will require specific design in conjunction with the WSE and are excluded.

## PLANNING AND DESIGN

### Scope and requirements

To supply the required quality and quantity of water to all customers as required by legislation and to the WSE’s minimum level of service. The design of the water network must be designed to meet:

- An acceptable water supply for each property, , by providing a service connection from the watermain to each property; and

Where the area is in an urban fire district, the required firefighting water supply to the general area, including fire flows for each property.

Designers must consider the hydraulic adequacy of the network including the specified levels of service, water quality and impact on the existing network.
The water network must meet the minimum design life requirements of 100 years taking into account structural strength, design loadings, seismic resilience, pressure transients, soil conditions and water conditions (internal and external corrosion). The designer must ensure the water network is cost efficient over its design life while accounting for environmental and community impacts through integrated three waters management and water conservation.  The designer shall ensure the WSE’s requirements for condition assessment to assess its condition when nearing the end of its design life are met to optimize future renewal strategies.

### Stage 1 Concept Plan Approval

A concept plan shall be developed for each project complying with the Entity’s three stage approval process set out in its Development Code, section 3 Figure 1 and 3.2 Information Requirements.

Depending on a WSE’s requirements and/or scope of a project, the plan format may vary from a layout sketch for a single dwelling connection to a complete system specification. For example, a plan for a reticulation system may simply require notification of the point of connection, service pressure and any special system requirements.

The concept plan for developments that trigger the Development Code criteria for Stage 2 and Stage 3 approvals processes  shall also:

- Satisfy requirements of relevant Health & Safety, Environmental Legislation and/or Regulations;

Address route and/or layout of reticulation, the operations and maintenance of which have the potential to cause traffic disruption especially in potentially congested areas such as CBDs and commercial areas;

Address the safe shutdown and maintenance of the system for maintenance;

Minimise the likelihood of pipe, fitting and appurtenance failures;

Early engagement with FENZ is recommended to address matters that relate to firefighting water supply

Identify any special requirements of the WSE or Regional or District Plan including, but not limited to:

- Provision for future expansion of the system and/or required augmentation of the existing system; and

The plan shall also consider and address as necessary:

Heritage and archaeological aspects.

Land ownership and planning requirements.

Impacts on community.

Water quality performance.

### Stage 2 Engineering Plan Approval

#### Designer’s needs and responsibilities

For developments requiring a Stage 2 Approval under the Water Services Act 2023 the Designer shall satisfy themselves at an early stage of the adequacy and accuracy of the Approved Concept Plan. The Designer should liaise with the WSE, prior to commencement of design, to ensure that sufficient planning is completed in order to undertake the design.

Drawings and Figures included in this NEDS a“d "typical drawi”gs" made available to Designers by the WSE shall be considered “s "typi”al" “r "conc”pt" and are not suitable for construction without further engineering design detail and being made project specific as part of the Construction drawings.

The Designer requires information such as:

- Concept Plan capacity assessment including:

  - Details of acceptable connection point(s);

  - Details of available flow (Q) at the connection point

  - Details of available pressure / head (H) at the connection point

  - Minimum and maximum allowable operating (working) pressure

Infrastructure servicing repo

rt

Details of any larg“r "through ma”ns" required for future expansion

Special requirements for firefighting purposes

Backflow risks

Water supply zone boundaries; and

Options to be considered for security of supply or alternative supply arrangements

#### Requirements to be addressed

The design shall provide a water supply to each property by way of a connection point to a water main or a pre-laid property service from a water main and shall address- the following, but not limited to:

- WSE’s policies, customer charters and contracts

WSE’s standards, specifications, design guides not otherwise contained or referenced by this NEDS, including pre-existing documents pre-reform included in the table in Appendix B.  Whichever is the more onerous shall take precedence unless the WSE allow a dispensation;

Applicable consents, District Plan & Regional Plan Rules

Hydraulic adequacy of the system

Ability of the water system to maintain acceptable water quality to the NZDWS and protect against backflow risk

Structural adequacy of system components for the design life

Ground conditions expected to be experienced during construction and over it’s design life

Ease of operation and maintenance of pipeline system components

Health and Safety (H&S) requirements, including safe access for operators and during maintenance

Environmental requirements including community impact of the works

Give effect to  Te Mana o Te Wai principles including minimum practicable adverse environmental and community effects

Consider any environmental and climate changes through the life of the asset in terms of sustainability, asset renewal, future access, and levels of service

A Safety in Design review and register shall be produced

Easement requirements

Minimisation of life cycle costs

Consideration of low carbon solutions

Resistance of each component to internal and external corrosion or degradation for the design life

System flexibility and robustness to functional changes

Constructability and methods of construction

Climate requirements (e.g., Alpine and/or frost areas)

#### Design outputs

The design output shall include, but not be limited to:

- Design Drawings showing, as appropriate, location of pipelines, valves, hydrants, metering, backflow prevention devices, pipe materials, size, pressure class, jointing methods, and corrosion protection measures.  Pipelines of and greater than 250mm diameter require long section drawings.

Detailed construction drawings including the location of all relevant obstructions, services, and structures.

Specifications for products, materials, site investigation, excavation / trench details and other technical matters.

Design Documentation of assumptions, constraints, and issues relevant to the design and not otherwise noted in the Concept Plan Approval or Design Drawings or Specifications for construction.

The Safety in Design register.

Other documents if required by WSE such as a construction inspection and testing plan, a whole of life cost estimate for the asset

### Design life

All water supply system buried assets shall be designed and constructed for an asset life of at least 100 years.

Surface boxes shall have a minimum design life of 50 years.

Some components such as metering, control valves, and control equipment may require earlier renovation or replacement.

The WSE list a number of accepted and standardised materials. The use of components not listed on the material supply standards or approved products registers requires specific approval from the WSE prior to their use through an application for a dispensation.

### Carbon Reduction

The Climate Change Response (Zero Carbon) Amendment Act 2019 sets a domestic greenhouse gas emission target for Aotearoa New Zealand to reduce net emissions.  To help achieve this target the WSEs will specifically encourage innovative solutions that reduce operational and embedded carbon emissions while maintaining secure, safe, resilient and enduring water reticulation assets.

# SYSTEM PLANNING

## GENERAL

### Structure plan/Infrastructure Master Plan

The Unitary, City or District Authority may live zone land or facilitate a district or structure plan setting out certain information to be used in design, such as population to be served, flows, sizing, upstream controls, roading, recommended pipe route layout, or particular requirements of the WSE. Where a district or structure plan is not provided, the designer shall determine this information by investigation using this National Engineering Design Standards (NEDS), engineering principles and by discussion with the WSE as necessary.

### Future development

Where further subdivision, adjacent to the one under consideration, is provided for in the District or Unitary Plan, or the developments is staged, the water supply infrastructure must be designed to cater for future development and incorporate such additional infrastructure as may be required to enable a staged development.

Planning horizon

This shall be determined by the Entity.

Concept plan

This shall be submitted for Stage 1 Concept Plan Approval to the Consenting authority and the Entity.

## SYSTEM CONFIGURATION

### Point of Supply

Points of connection shall conform to WSEs requirements and any relevant Bylaw or other legislative instrument.  The Entity may issue an indicative layout plan with functional design requirements for any specific project. Provision for a meter, whether required by the Entity or not, shall be included in the design to enable easy retro-fitting in the future.

The design of the reticulation shall be such that one water supply connection can be readily provided to the ‘front’ of each allotment but avoid the potential driveway or vehicle crossing location.  
The point of supply is after the last fitting of the master meter, manifold or WSE owned backflow prevention assembly at the property boundary. All equipment and fittings upstream of this point are owned by the water supply entity and are considered part of the water supply entity’s network.

For front properties, service connections shall be located at the centre of the road frontage or adjacent to vehicle entrances, outside of the property boundary. For a rear lot serviced by an access strip or ROW, the service connection shall be located adjacent to the vehicle crossing entrance, outside the property boundary.

The point of supply to the consumer is shown on Drawing WS-01 which contains examples of these from across the country.

- The service connection shall have a meter (if required by the Entity), a manifold incorporating a toby valve and non testable backflow preventer under a WSE accepted meter box located in the road reserve, 300mm from the boundary and the supply connection shall be extended a minimum of 1m inside the boundary (refer to Drawing WS-18, etc).  Note: All testable BPD shall be installed above ground as part of a backflow prevention assembly.

Where there are between two and four lots on a right of way, or in certain cross lease or duplex situations an appropriately sized manifold box and lid is to be used. The manifold box shall be located in the right of way clear of vehicle traffic movements and adjacent to the vehicle crossing

Where five or more service connections will be required in an access lot or right of way, a single pipe shall be used, subject to the following design criteria:

- A rider main of DN63 PE shall be used, or the rider main diameter shall be determined by firefighting requirements if applicable.

Service pipes crossing the access lot shall be DN25 PE and shall be placed in a DN50 duct

The service pipe connections to the rider main shall be in the grass berm

Service connections, meters (where applicable), manifold boxes and gate valves shall be constructed to Drawings WS-16 to 20

The rider main shall have a 50NB flushing valve of the furthest point from the reticulation. Refer Drawing WS-01

Metallic detector tape, laid directly above the rider main at a maximum depth of 200mm is required where the alignment of the pipe is not clearly defined as a straight line between valve box lids and in other circumstances as required by Council

An "Easement in Gross" over the right of way shall be granted in favour of the entity for water supply purposes to allow access for maintenance of the rider main and connections

Ownership of the rider main shall transfer to the water supply entity. The Entity’s responsibility for maintenance of the service pipes shall cease at the boundary to each individual lot

Refer to Drawing WS-01 for connection layouts

In some cases, if a fire hydrant is required to comply with NZ Fire Service Firefighting Water Supplies Code of Practice PAS NZS 4509, then the Entity will own the hydrant and the main up to the hydrant and be provided with an easement over these assets.

With the exception of c) and d) above, the Water Supply Entity does not own or operate pipelines on private property. Unit Title developments are recommended to conform to service connection layouts described above in order to facilitate for subsequent sub-division should this be required as a future development of the site.

Isolation valves for individual units are required  to comply with Building Code Acceptable Solutions G12/AS1 Paragraph 5.5.1 and G12/AS3, which cites AS/NZS 3500 Part 1: 2021 Clause 5.4.4 Water services.  They ) shall be located outside of the building platform but within the property. For avoidance of doubt, these shall be considered to be private.

The connection should be designed to suit the existing reticulation layout, and any future development, and be supported with an approved Concept Plan as described herein and the Development Code.

Connection of a new development may require upgrading or extending the existing water network so that the existing levels of service are maintained.

Cross connections between any other water supply are prohibited.

## SYSTEM PLANNING PROCESS

### General

System planning shall ensure sufficient supply is provided for the land area, number of properties and population projections in the area of supply

The water demand allowance in the subdivision design shall include provision for:

- Population targets

The area to be serviced; or

Individual properties proposed by the developer.

NZS 4509 - New Zealand Fire Service Firefighting Water Supplies Code of Practice (where required by the WSE).

Adjustment may be required to cater for the known performance (demand-based flows) of the existing parts of the water system.

### Extending / upgrading an existing water supply system

Alteration to existing infrastructure

The connection of new developments may require upgrading or extending the existing water network and must maintain the minimum level of service for the existing infrastructure. Alteration to the existing water network to achieve the required level of service and standards for development outside of the on-demand water supply areas, the water supply area or restricted flow area must be at no cost to the WSE.

In order to extend a water supply into an adjacent development, the Developer shall undertake the following actions working closely with the WSE who may undertake some or all of these actions with their own models and staff:

- Assess the system capacity and operating characteristics at potential connection points by considering:

- available pressure head, H;

available flow, Q; and

water quality performance of the system

firefighting capacity of the system.

Perform a network analysis to:

- assess the adequacy of the existing system to service the new development

- determine the impacts of the new development proposal upon the existing system, including local and associated remote system elements

determine capacity augmentation / replacement and/or operational requirements e.g., changed controls

determine additional water quality infrastructure and/or operational measures required; and

assess options of alternative supply and continuity of supply.

Assess proposed works in the light of future stages of the development and other separate (contiguous and/or adjacent) developments.

Plan the distribution network e.g., layout, hydraulic design (Refer to sections 3 and 5 of this NEDS)

Plan the localised reticulation networks for the new development (Refer sections 3 and 5 of this NEDS).

### Providing a new water supply

New water sources are not in the scope of this NEDS.

### Non-drinking water as drinking water substitution

Grey water or non drinking water systems are not in the scope of this NEDS.

## DEMANDS

### General

Water reticulation systems shall be designed to supply peak flow requirements for residential, non-residential, and firefighting water demands.  Residential and non-residential demands shall be calculated following sections 2.4.3.3 and 2.4.3.4 while firefighting requirements shall comply with NZS PAS 4509.

As development continues or demand management initiatives are enacted, pressures in water supply networks are likely to reduce over time.  To accommodate these future changes water supply networks shall be designed to maintain appropriate nominated pressures but also to meet demand at the minimum network service pressures from Section 2.5.3.3 or a100kPa minimum head under firefighting flow conditions.

Any shortfall between the fire flow and pressure required by the proposed development and the minimum design supply pressures and flows shall be the responsibility of the site owner.  In such cases the site owner shall provide alternative fire protection services, such as private storage and pumps, at the cost of the site owner.

Many commercial and industrial developments require installation of special fire protection services. While it is the responsibility of the site owner to provide these fire services, the developer shall design the water reticulation system with consideration to the required demands, where these are known in advance, by taking into account land zonings, SNZ PAS 4509 requirements and the minimum design flows and pressures as stated in sections 3.1 and 2.5.3.3. The site owner shall ensure that if any special fire protection services require supply of water from the WSE’s reticulation network, the design shall include the protection of existing WSE assets and consider the existing and future available pressure and flow during normal operations.

### Multiple water supply systems

These are not in the scope of this NEDS as this situation will require engineering design. However, developments that include an additional water supply source or sources shall use design criteria from sections 2.4.3 and 2.4.4 to calculate peak and average residential and non-residential demands.

Where a property has an additional water supply system, or systems, the property shall be considered high hazard for backflow prevention and require a RPZ backflow prevention assembly (or suitable backflow prevention solution) at the point of supply from the drinking water system. This applies irrespective of if the additional source is reticulated, a rainwater tank, a private bore or other source..

#### Rainwater tanks

Rainwater tanks are not in the scope of this NEDS.

### Demand assessment

#### General

The water reticulation system shall be designed to comply with SNZ PAS 4509, where required by the WSE.

Any shortfall between the fire flow required by the proposed development outside the WSE’s minimum design supply pressure and flow is the responsibility of the site owner, who is to provide alternative fire protection services, at their own cost. (refer to Section 3.1 for more details).

Demand assessment shall include the peak and average daily residential and non-residential flows excluding any firefighting water requirements.  Each development shall have individual calculations for the demands.  However the full analysis must include a fire flow scenario as defined in SNZ PAS 4509 clause 4.2.

Future changes shall be considered during design.  Should a development include large properties that could potentially be subdivided further in the short to medium term the design shall be based on the future number of properties.

Overall average demand shall be the sum of residential and non-residential demands.

#### Minimum flows

The minimum flow shall be the greater of:

- 25 L/min at the customer point of supply

Hydrant fire flow, refer to SNZ PAS 4509

The network shall be designed to maintain appropriate nominated pressures at the minimum design flows.  For water mains (typically 100mm or greater nominal bore fitted with fire hydrants) the minimum design flow rates for reticulation to serve a development shall be calculated following the equation:

Minimum Flow Ls=Maximum of Peak Hour Flow   OR23×Peak Hour Flow+Firefighting Flow

Where firefighting flows are determined by SNZ PAS 4509 - New Zealand Fire Service Firefighting Water Supplies Code of Practice, submains and other pipes smaller than 100mm nominal bore shall use the peak hour flow as the minimum design flow.

#### Residential

Average daily residential demand calculations shall include the number of properties, number of residents at each property and the average daily water demand per person following the equation:

Average Residential Demand m3d=Number of Properties ×Occupancy × Consumption1000

The number of properties shall include the total number of residential zoned properties proposed in the development, or for large properties that may be subdivided further in the short to medium term, the design shall be based on the future number of properties.
Occupancy numbers from the Table 2-1 below shall be applied.

| Table 2-1 - Residential Design Occupancy Allowances |  |
| --- | --- |
| Number of Bedrooms | Occupancy for Design Purposes |
| 1 | 2 |
| 2-4 | 3 |
| 5+ | Specific agreement with Entity |
| Unknown | Assume a design occupancy of 3 per dwelling unit |
| Notes: Where large dwellings are proposed, which have additional rooms beyond those allocated as dining, lounge, and bedroom e.g., family, office, study or sleep outs which have the potential to be used as bedrooms, an additional occupancy allowance should be made on the basis of 1 extra person times the ratio of the total floor area of the additional room(s) to that of the smallest designated bedroom. For residential retirement villages without a hospital facility and that have single bedroom units then a design occupancy rate of 1.5 may be considered for all units. |  |

- Average daily consumption figures for the specific network shall be provided by the WSE.

Where figures for the network are not available assume:

- 275 L/person/d for networks with universal metering and volumetric water billing

325 L/person/d for networks with no controls on water use

200 L/person/d for residential apartment buildings

#### Non-residential

Non-residential (commercial, industrial, or reserve) area design flow rates shall consider land area, lot sizes, land use type and requirements of individual businesses.  Reserve, park, and sports field flows shall consider climate and rainfall and may require expert advice on irrigation requirements for plants or grass.  Non-residential design flows require WSE approval prior to commencing detailed design.

| Table 2-2 - Non-Residential / Other Facility Design Occupancy Allowances |  |  |
| --- | --- | --- |
| Commercial Facility Types | Design Water Flow Allowance |  |
| Hospitals | Day Facility (treatment facilities, wards) | 320 Litres per bed per day |
|  | Night and Day Facility (24-hour operation) | 630 Litres per bed per day |
|  | Staff | 50 Litres per employee per day |
| Child Day Care | Children | 45 Litres per child per day |
|  | Staff | 50 Litres per employee per day |
| School (day students) | Primary School | 20 Litres per student per day |
|  | Secondary School | 25 Litres per student per day |
|  | Staff | 50 Litres per employee per day |
| School (boarding) | Secondary School | 160 Litres per student and staff member per day |
| Student Accommodation |  | 160 Litres per student per day |
| Motels and Hotels | Guests | 200 Litres per room per day |
|  | Staff | 50 Litres per employee per day |
| Community halls and churches and/or facilities with intermittent use |  | 12 Litres per seat per day |
| Note: For activities where a large number of people can be expected to use multiple water fixtures simultaneously e.g., community halls and conference halls, the Peaking Factor shall be based on the number of water fixtures / appliances, as per NZS 3500.1 Plumbing and Drainage: Part 1: Water Services. Water consumption allowances in this table include general irrigation (but not specific irrigation systems) and grounds upkeep. |  |  |

| Table 2-3 – Other Facility Design Occupancy Allowances |  |
| --- | --- |
| Number of Bedrooms | Occupancy for Design Purposes |
| Dry retail (Note 1) (where kitchen/toilets are not normally made available to customers) | 1 person per 50m2 nett floor area at 65 litres per person per day. |
| Office buildings and dry retail where toilet facilities, etc. are provided to customers. | 1 person per 15m2 nett floor area at 65 litres per person per day. |
| Wet retail (Note 2): Food and or beverage retail/preparation e.g., coffee shop, restaurant, bar, butcher, fresh fruit, and vegetable retail. | 15 litres per day per nett m2 of floor area (including kitchen and dining areas). |
| Notes: 1) Dry retail is where water is normally only used by staff for their own personal food preparation/toileting needs. Examples include clothes shops, hardware retail. 2) Wet retail is where water is used to prepare food product for customers. Examples include cafés, lunch bars, restaurants, butcheries, fresh fruit and vegetable retailers, food courts, bars and supermarkets. 3) Assuming no significant irrigation. Important: Nett floor area is the total floor area of the building (exclude any open land areas), less non-productive areas, such as: lobbies; lifts; machine rooms; electrical services; stairwells; fire escapes; corridors and other passages used in common with other occupiers; car parking areas; etc. If the nett area is unknown, and the type of buildings are unknown, it can be assumed that the nett floor area is = 80% of the gross floor area of the building. As a guide to how activities will be assessed, commercial washing activities such as car / boat washing activities, etc. would be regarded as a “wet-industry” and not as a commercial wet retail activity, as the water is being used as a part of a process (washing). Large-scale food-processing (i.e., for supply to commercial customers, as opposed to on-site retail customers) would be regarded as an industrial activity. Preparation / manufacture of non-food based products is also regarded as an industrial activity. Industry design flows are detailed in the section below. |  |

| Table 2-4 – Wet & Dry Industrial assumed Design Allowances |  |
| --- | --- |
| Industry Activity Type | Routine Peak Daily Usage Litres per square metre per day (L/m2/d) |
| Light water users, or up to 2 storeys (Note 1) | 4.5 |
| Medium Water users, or 2 to 5 storeys (Note 2) | 6 |
| Heavy water users, or 5 to 10 storeys (Note 3) | 11 |
| Very heavy water users (Note 4) | >11 Specific design required |
| Notes: 1) A light water usage industry is a relatively dry and clean trade where industrial practices do not include process water usage. Showers provided for personnel’s ad-hoc use would still fall into the ‘light water user’ category. 2) A medium water use industry is a dirty trade where good practice requires regular water usage. Showers are in daily use because commercial activities require staff to have washing facilities. There is no process water usage. 3) A heavy water use industry uses water as a part of commercial activities in moderate quantities, but is not a Wet Industry, as defined in note 4 below. Wherever possible, the design flow for a heavy water usage industry should be checked against known water consumption rates. The Design Engineer shall submit evidence of these checks as a part of the application. 4) A very heavy water usage industry is a trade using in excess of 12 L/m2 of nett floor area/d on a routine basis. 5) This table assumes no significant irrigation. |  |

### Peak demands

Water demands vary on a regional basis depending on climate conditions and consumer use patterns. The WSE may provide historically-based demand information appropriate as the basis for design.  Where such flow data is not available the Designer shall agree the method for calculating peak flows with the Entity.  The following may be used as default values.

Peak Day Demand (over a 12-month period) = Average Day Demand x Annual Day Peaking Factor (ADPF)

Unless specified otherwise by the WSE:

- ADPF = 1.5 for populations over 10,000

ADPF = 2 for populations below 2,000

Interpolated between 1.5 and 2 for populations between 10,000 and 2,000

Peak Hourly Demand = Average Hourly Demand (on peak day) x Peak Hour Peaking Factor (PHPF) over a 24-hour period

Unless specified otherwise by the WSE, the PHPF shall be 2.5.

Peak flow calculation example:

For a new land subdivision of 50 three bedroom dwellings use:

Design Population = 50 dwellings x 3 people = 150 people

Average daily demand = 150 x 275 = 41,250 L/d

Peak day demand = 41,250 x 2 =82,500 L/d

Peak hourly demand = (82,500 / 24) x 2.5 = 8,594 L/h

= 8,594 / 3,600 = 2.4 L/s

## SYSTEM HYDRAULICS

### General

The diameter, material type(s), and pressure class of the water main shall be selected to ensure that:

- The main has sufficient capacity to meet peak demands while maintaining minimum pressure

All consumers connected to the main receive at all times an adequate water supply flow and pressure

The appropriate fire flows and pressures can be achieved (see Section 2.4.3)

Flow velocities are sufficiently low to minimise pressure losses

Flow velocities are sufficiently high to minimise water age

A properly designed hydrant flow test can provide information about the current capacity of the water supply system to the area where the development is proposed and the capability of the hydrant asset to deliver required flows. This information is essential to support the capacity assessment process regardless of the fire-fighting requirement of a building.  However if the WSE have a fully calibrated and up to date model this test may not be required.

For the design of all commercial, industrial, and residential small developments as deemed required by the WSE, actual hydrant flow tests shall be carried out by an approved person at peak hour, with pressure recorded at the nearest public hydrant and the next available hydrant flowing in a fully open position.  All at the developers cost.

The design of hydrant flow test shall not extract flow from hydrants beyond minimum flow targets. Refer to Section 2.4.3.2.

All hydrant flow tests require WSE approval prior to conducting in the field. The WSE may require the hydrant flow test to be observed in the field by an approved independent observer to audit the readings. If at any time during a hydrant flow test the observed pressure drops to or below 10m, the hydrant flow test shall be ended. The hydrant flow test shall also follow a procedure to:

- Maintain public safety and damage to property

Prevent contamination incidents

Prevent discharge of excessive amount of chlorinated water into the environment

Prevent suspension of sediment and its discharge to stormwater systems

Prevent scouring of surfaces

No hydrant check is to be planned without that plan being approved by the Entity.  Note that generally only hydrants painted yellow can be used for hydrant flow tests.

### Network analysis

Where required by the WSE, a network analysis of the system shall be undertaken at a developer’s cost to ensure adequate water supply is available to all consumers connected to the system for all defined modes of operation. The analysis shall include all elements within the system, including current and future development stages in a multi-staged development site, and the analysis shall address all demand periods including peak demand, low demand flows, and fire flows. Future demand should be assessed separately to the staged development scenarios to account for potential maximum infill development (refer to section 2.4.3.1.  The analysis should also ensure interruptions to supplies are limited during cut-ins and network extension activities.  The network analysis shall be provided in the design documentation report (refer 1.2.3) detailing any assumptions.

### Operating pressures

#### Service pressure

Service pressure is location and flow-rate dependent. At any point in the system, service pressure is dependent on the available static head or steady state pumping pressure less hydraulic losses due to demand flows. Service pressure should be specified by the WSE. Where service pressure limits are not specified, the limits in Table 2-5 shall be adopted for reticulation mains.

#### Maximum allowable service pressure

An upper limit on service pressure is generally imposed to reduce wastage of water through leakage and to minimise the risk of damage to consumer appliances connected to the water supply. Transfer mains and those distribution mains that do not supply directly to consumers may operate at higher pressures than reticulation mains, e.g., up to 3500 kPa (350 m head). An operating pressure limit may be specified by the WSE. Where a transfer or distribution main supplies directly to the reticulation system, the maximum allowable operating pressure is set by the maximum service pressure and shall be as specified by the WSE or in accordance with the requirements of Table 2-5, whichever is applicable.

Where the maximum service pressure exceeds that in Table 2-5 the Designer shall address the need for pressure reducing facilities.

#### Minimum service pressure

A lower limit on service pressure is usually specified to provide sufficient pressure for the design flow to be delivered onto properties. This includes an allowance for overcoming the basic head losses in the water service, associated fittings, meters, and backflow prevention devices. An additional minimum head for industrial/commercial area shall be included to allow for the likely requirement to install (high-head loss) backflow prevention devices on these properties' services and to provide some allowance for greater water service head losses in these generally larger properties.

| Table 2-5 - Service Pressure Limits for Drinking Water Supply |  |  |
| --- | --- | --- |
| Pressure | Application |  |
|  | Residential | Industrial/Commercial |
| Maximum Service Pressure (see Notes 1 & 2) | 800 kPa (80 m head) | 800 kPa (80 m head) |
| Minimum Service Pressure (see Note 3) | 250 kPa (25 m head) | 250 kPa (25 m head) |
| Notes: - AS/NZS 3500.1 requires that the maximum static pressure at any outlet, other than a fire service outlet, within a building does not exceed 500kPa (50m head). - Pressure into properties is dealt with in the Building Code, not in the NEDS which refers to public infrastructure only. Maximum allowable service pressures may be different in each supply zone based on operations and leakage minimisation. - The WSE may specify alternative minimum allowable service pressures to provide a different service standard. A higher minimum service pressure may be specified in Central Business Districts (CBDs)s or for industrial / commercial areas. Where flows from fire hydrants are a major component of the flow, a lower minimum pressure but no less than 100kPa may be accepted. Near reservoirs or diurnally in rural areas, the minimum service pressure may be reduced to ensure an economical system design. In these cases, larger pipe sizes may be required to ensure reasonable flow to each property. In some cases, the property owner may be required to install a private storage tank and an on-property pressurising system. |  |  |

#### Average service pressure

##### General

Service pressures within supply zones may vary widely between properties, in maintaining these pressures within the limits specified inTable 2-5, depending on the relative levels of the properties compared to that at the supply source (such as Bottom Water Level (BWL) of a reservoir or the level setting of a Pressure Reducing Valve (PRV). For example, service pressures may always be close to the maximum for relatively low levels close to the source but always close to the minimum for relatively high properties. Various measures may be included in the system design to either limit the high pressures or ensure a reasonable range of pressures are available under average operational conditions.

##### Limiting High Average Service Pressures

Where large portions of a network will be subject to pressures close to or above 80m head, the WSE may also set a maximum value for an average service pressure to reduce potential system leakage. Typically, this would apply when pressure can be reduced by relatively simple infrastructure measures and at reasonable incremental cost.

##### Ensuring a Suitable Range of Service Pressures

The WSE may specify a limiting ground level, related to the supply source level, such that relatively high properties within the supply zone will receive pressures a defined amount above the minimum values, at some time within the diurnal operation of the supply. This ground level may be defined by the WSE using concepts such as Minimum Static Head (typically subtracted from the Bottom Water Level (BWL) of a reservoir) or consideration of typical head losses through the supply network (subtracted from a defined low operating level of a reservoir) to achieve the required minimum pressure (including, as required, an extra pressure allowance above the design minimum pressure). If the WSE uses the minimum static head concept and does not specify the limit to be used, consult the Entity for clarification e.g., use the values in Table 2-5.

### Pressure variation analysis

An assessment shall also be made of diurnal pressure variations occurring under normal operating conditions with a view to minimising impacts on customer service, system leakage and minimise the risk of pipe failures.
Where required by the WSE, water distribution and reticulation systems shall be designed to control diurnal pressure variations. The restriction of diurnal pressure variations may be specified by the WSE within a set percentage of the normal operating head of the system, or other limit. Variations may be reduced by measures such as:

- Supplying a sufficiently large and interlinked network to reduce the effect of demand peaks

Limiting the range of elevations served from each water main

For PRV zones, ensuring a sufficient number of customers to maintain sufficient minimum flow for the PRV to operate effectively.

The cause of any significant pressure surges or high-pressure areas in an existing or proposed supply system shall be identified and design solutions proposed. Excessive surges can reduce the life of some products and increase customer complaints.

### The WSE shall specify whether a surge analysis is required in any functional design requirements. A surge analysis of the system shall be undertaken for zones affected by pressure variations e.g., pumped mains, locations affected by control valves, downstream of pressure reducing valves. The system shall be analysed for the full range of anticipated rates of change of flow to determine the magnitude and frequency of surge pressure in the system.

Determining supply zones

All areas will have limits of acceptable site ground elevation and/or pressure requirements in a water district zone due to hydraulic grade line (HGL) constraints. In some cases, the installation of a pressure reducing valve to create a pressure reduced zone or the installation of a pump station to create a pressure-boosted zone may be considered to control the pressure delivered to an area. In these cases, the Designer shall consult the WSE to confirm if the proposal is acceptable for long term operations.

Pressure management in the water network supports longevity of assets and reduces the need for reactive repairs or increased unaccounted for water losses resulting from excessive operating pressures. PRVs may require pressure and flow monitors and actuation of the valve to eliminate pressure transients.

Long-term cost/benefit analysis of a PRV or booster pump station may be required by the WSE for assessment of the proposal.

## WATER QUALITY

### General

A number of factors in a network can adversely affect the quality of the water in the system. The network design shall ensure that the water quality supplied at each property maintains applicable compliance with the Water Services Drinking Water Standards for New Zealand Regulations 2022.  The design shall include backflow prevention measures as  required by Taumata Arowai Drinking Water Quality Assurance Rules, 2022.

All parts of the water supply system in contact with drinking water shall be designed and constructed using components and materials that comply with AS/NZS 4020 (Revised 2018) and are on the Entity’s Approved Products Register.

### Prevention of Backflow

Drinking water supply systems shall be designed and equipped to prevent backflow. The location and operation of hydrants, air valves, and scours shall ensure no external water enters the system through negative pressure from normal operation.

Testable backflow preventers must be tested by a registered independent qualified person (IQP) under the Building Act 2004  Health (Drinking Water) Amendment Act 2007, and Water Services Act 2021R Backflow prevention shall be installed on all water supplies at the boundary proximity between public and private pipe ownership (point of supply).

Standards and guidance on this topic are contained in the following documents:

- AS/NZS 2845.1 (2022) Backflow prevention devices, Part 1: Materials and design performance requirements

Boundary Backflow Prevention for Drinking Water Supplies. Water NZ. 2019. https://www.waternz.org.nz/Article?Action=View&Article_id=48

Acceptable Solutions and Verification Methods for New Zealand Building Code Clause G12- Water Supplies

The preferred location of backflow devices is within 500mm of the property boundary in the public road reserve to allow access for ongoing maintenance and inspection. Where this is not practicable the backflow prevention device may be installed in private property within 1m of the property boundary. There may be no other connection upstream of the backflow preventer. Source backflow prevention requires special certification and must consider suitable accessibility for maintenance and certification.

Ownership of the backflow prevention device will be as agreed with the WSE.  Any agreements shall include arrangements that will allow the WSE access to test the device upon request at any time. Where access is prevented, the WSE may act in accordance with this clause. Regardless of ownership or location, the cost of installation, maintenance and annual certification is borne by the private property owner.

Any service lead shall be installed with, as a minimum, a dual check valve. Depending on the property risk profile the backflow prevention device may need to be upgraded accordingly at time of connection/meter installation, or at any time when the supply risk level changes.

All private fire supply systems shall be fitted with a suitable backflow prevention device. The minimum risk level for fire systems shall be medium, but considered high risk level for fire suppression systems with chemical additives.

Cross connection hazards and hazard rating shall be to G12/AS1, Section 3.0 of the Building Code. The complete site must be surveyed to determine the backflow hazard rating level.

The types of devices shall be considered based on a risk assessment undertaken according to the Building Code clause G12, Water Supplies.  The table below, is taken from guidance provided in Boundary Backflow Prevention for Drinking Water Supplies, Water NZ May 2019 (residential households may be considered in the very low risk category):

| Table 2-6 -Device types to be considered for backflow prevention |  |  |
| --- | --- | --- |
| Hazard Level | Boundary Device | Source Device (special certification with WSE) |
| Very Low Risk | Non testable dual check valve |  |
| Low hazard | Dual check valve | Dual check valve Vacuum breaker |
| Medium hazard | Double check valve Double check detector | Double check valve Spill proof vacuum breaker |
| High hazard | Reduced pressure zone Reduced pressure zone detector | Reduced pressure zone Registered air gap |

Backflow preventer devices shall comply with the requirements of the WSE’s material supply standard. When a connection is made to the WSE’s local water supply network an approved IQP shall test and certify the backflow preventer.

The WSE will intervene and the water supply shall be restricted in accordance with the Local Government Act 2002, the Building Act, Water Services Act 2021 and the relevant WSE Network Bylaw or other legislative instrument under the following circumstance, but not limited to:

- Unprotected supply with direct or indirect connection to possible contaminants

Where the level of risk increases (change of use) and the device is not upgraded accordingly

Where the device is not suitable or suitably installed for the level of hazard protection

Expired backflow prevention device certification

If there is a risk of backflow in a reticulated drinking water supply, the drinking water supplier may—

install a backflow prevention device and require the owner of the premises to reimburse the supplier for the cost of installation, maintenance, and ongoing testing of the device; or

require the owner of the premises to install, maintain, and test a backflow prevention device that incorporates a verifiable monitoring system in accordance with any requirements imposed by the supplier.

### Water age

Drinking water supply systems shall be designed to minimise water age in the network to ensure no unacceptable deterioration of water quality. This shall include:

- Mains with dead ends (or termination points) shall be avoided by the provision of looped watermains. Particular care shall be taken at the boundaries between supply zones where dead ends shall be avoided or minimised whilst maintaining existing district zone boundaries

Mains for short runs shall be reduced in size or looped, for example no-exit roads (see Figure 5-6)

The WSE may at its discretion require the developer to implement a system to improve the water quality where development uptake versus overall size affects the water grade of the area. This may be in the form of temporary dosing systems and flushing. A development staging strategy shall be provided to the WSE with commitment to provide for any associated costs before connecting to the Entity’s system.

Water sampling points shall be provided as required by the WSE.

### Disinfection

Each WSE will instruct on disinfection procedures to be followed.  Part Two of this NEDS provides guidance in Chapter 20, which is based on Watercare’s Code of Practice for Disinfection of Water Systems No.COP-04, Version 4, August 2022.

## PUMPING STATIONS

Pumping stations require specialist designs and require significant lifetime operations and maintenance expenditure by the WSE.  Any proposal and design shall be prepared in consultation with and meeting the particular requirements of the WSE.  Therefore, they are not included in the scope of this reticulation NEDS.  In any case pumping should not be used a s solution for meeting fire fighting requirements.

## SERVICE RESERVOIRS

Service Reservoirs require specialist designs and require significant lifetime operations and maintenance expenditure by the WSE.  Any proposal and design shall be prepared in consultation with, and meeting the requirements of, the WSE.  Therefore, they are not included in the scope of this reticulation NEDS.

## TRENCHLESS TECHNIQUES FOR PIPELAYING

Trenchless techniques for pipelaying in both greenfield and brownfield developments can improve sustainability outcomes, reduce greenhouse gas emissions by reducing fuel consumption and reduce traffic impacts.

Various methods are available, and Guidelines and Specifications are in AS/NZS2033:2023 Installation of polyethylene pipe system.  Horizontal directional drilling (HDD), Pipe bursting, microtunnelling, pipe jacking, thrust boring are all potential methods to lay pipelines without the need for long, deep, disruptive excavations which may be considered.  However, any trenchless technique shall be evaluated against at least the following effects before a decision on its suitability is reached by the WSE:

- Effect on Te Mana o te Wai principles and values described in the Frontmatter to this NEDS

Effects on environmentally sensitive areas

Impact on built up or congested areas where minimizing traffic disruption is critical

Suitability for crossings

Sustainability outcomes

Long term maintenance

Ground conditions

Presence of other buried services

## FUTURE SYSTEM EXPANSION

Any proposed reticulation system that is large may have long term issues to be resolved in the initial concept stage, such as staging, water quality with low initial demands, future stages requiring a different water source, storage, pumping which all need to be understood before the first reticulation is designed and built.

The developer will provide the WSE with a concept plan covering all stages of a planned development before any approval process may begin.

## SYSTEM REVIEW

To be written after the LD group report on the 3 stage approval process is available

# HYDRAULIC DESIGN

## SIZING

### General

Inputs to the design process shall include:

- Hydraulic grades (HGL) at point of connection to existing WSE’s network

Existing system hydraulic capacity

Proposed land use, zoning, area to be serviced, and water use activities

Water demand (low, average, peak) in l/s and m3/day,  including diurnal profiles

Fire flow requirements for the proposed site

Hydraulic head loss, including backflow prevention

An understanding of the general operating philosophy and design constraints of the water district zone the proposed development is connecting to; and

Elevation assumptions at proposed water points of connection (also customer meter locations).

The outputs of water main hydraulic design shall include:

- Size of watermains (nominal diameter);

Maximum, average and minimum design pressure at each of the points of connection (also water meter locations)

The pressure class/rating of pipeline system components

Surge analysis results, if required

Pipe head loss (m/km) and velocity (m/s) compliance with low, average, peak demand, and firefighting demand scenarios

Specification of the maximum and minimum allowable operating pressure

Flow and pressure compliance with low, average, peak demand, and firefighting demand scenarios

Reticulation layout that provides security of supply to end users.

### Minimum pipe sizes

By convention, most pressure pipes in New Zealand are usually referred to by their nominal internal diameter (i.e. DN50, 100, 150, etc.) whereas the equivalent size ISO dimension PE pipes are usually referred to and specified by their nominal outer diameter (i.e. 63, 125, 180 OD).

For general application, WSE’s have standard sizes for all watermains as shown in the Table 3-1 below.  Pipe sizes other than those listed below must not be used on the water supply network.  All trunk mains will require specific design in collaboration with the WSE.

| Table 3-1 - Standard sizes for watermains |  |
| --- | --- |
| Pipe type | Size and material |
| Connections | DN20, DN25, PE80, PN12.5 |
| Ridermains | 63 OD, PE80, PN12.5 |
| Principal mains | DN150 PVC or 180 OD PE100 , PN12.5. |
| Trunk mains | DN250 Series 2 PVC-O or DN315, PE100 (see note 2 below). |
| Notes: a) Trunk Mains >DN250 requires specific design in consultation with WSE. b) Some small/rural water supply schemes may allow 100mm diameter principal mains, only as agreed by the WSE. |  |

### Empirical sizing of reticulation mains

Table 3-2 and Table 3-3  may be used as a guide for sizing mains.

| Table 3-2 - Empirical guide for principal main sizing |  |  |  |  |
| --- | --- | --- | --- | --- |
| Nominal Internal diameter | Capacity of main (single direction feed only) |  |  |  |
|  | Residential (lots) | Rural Residential (lots) | General/light industrial (ha) | High usage industrial (ha) |
|  |  |  | - | - |
| 150 | 160 | 125 | 23 | - |
| 200 | 400 | 290 | 52 | 10 |
| 225 | 550 | 370 | 66 | 18 |
| 250 | 650 | 470 | 84 | 24 |

| Table 3-3 – Empirical guide for sizing rider mains |  |  |
| --- | --- | --- |
| 63OD Rider mains |  |  |
| Pressure | Maximum number of dwelling units |  |
|  | One end Supply | Two end supply* |
| High > 600 kPa | 20 | 40 |
| Medium 400 – 600 kPa | 15 | 30 |
| Low < 400 kPa | 7 | 15 |

### Fire flows

The water reticulation system shall be designed for the minimum design flows from 2.4.3.2, these include firefighting flows complying with SNZ PAS 4509. Hydrant numbering and spacing shall comply with SNZ PAS 4509.

Any shortfall between the fire flow required by the proposed development outside the WSE minimum design supply pressure and flow is the responsibility of the site owner to provide alternative fire protection services, at the cost of the site owner.

Many commercial and industrial developments require installation of special fire protection services. While it is the responsibility of the site owner to provide these fire services, the developer shall design the water reticulation system with consideration to the required demands, where these are known in advance and the minimum design as stated in Section 2.4. The site owner shall ensure that if any special fire protection services require supply of water from the WSE’s reticulation, the design shall include the protection of existing WSE assets and consider the existing and future available pressure and flow during normal operations.

As development continues in a zone, or as required by the WSE to manage the water supply system, the pressure and flow is likely to reduce. The design of special fire protection services shall also make allowance for a future upgrade at the site owner’s cost when the system operating pressure and flow changes in the future to other conditions within the WSE’s level of service criteria - refer to sections 2.4 and 2.5.

### Sizing by analysis

#### General

The diameter, material type(s), and pressure class of the water main shall be selected to ensure that:

- The main has sufficient capacity to meet peak demands while maintaining minimum pressure

All consumers connected to the main receive at all times an adequate water supply flow and pressure

The appropriate firefighting flows and pressures can be achieved

All pipe materials and design shall consider the nominal bore (NB) or internal diameter for design purposes where nominal diameter (DN) is referred to in this document.

#### Head losses

The head loss through the local network pipes and fittings at the design flow rate for peak day - peak hour, shall be less than:

- 5 m/km for DN ≤150

3 m/km for DN >150

Pressure pipe head loss shall be calculated using the Hazen-Williams, Mannings or Colebrook-White formulae for pipe internal diameter of ≥50mm NB and a flow velocity of less than 3 m/s.

#### Hydraulic roughness values

The hydraulic roughness values considered in the analysis shall take account of the pipe material proposed, all fittings and other secondary head losses, and the expected increase in roughness over the life of the pipe.

| Table 3-4 - Hydraulic roughness values |  |  |  |
| --- | --- | --- | --- |
| Material | Colebrook – White coefficient k (mm) | Manning roughness coefficient (n) | Hazen Williams Coefficient (C) |
| PE | 0.003 – 0.015 | 0.008 – 0.009 | 140 |
| Ductile iron concrete lined | 0.01 – 0.06 | 0.006 – 0.011 | 110-140 |
| Mild steel concrete lined | 0.01 – 0.06 | 0.006 – 0.011 | 130-140 |
| PVC | 0.003 – 0.015 | 0.008 – 0.009 | 145 – 150 |
| GRP | 0.003 – 0.015 | 0.008 -0.009 | 140 |
| NOTE: The values show a range of roughness coefficients. These represents the expected value range for clean, new pipes laid straight to typical maximum expected for aged pipes. It cannot be absolute maximum, as factors detailed in AS 2200 can lead to even higher roughness values in some circumstances. Recommendations on the appropriate roughness coefficient for a particular fluid may be obtained from the pipe supplier. Refer also to AS 2200 table and notes. |  |  |  |

#### Flow velocities

In practice it is desirable to avoid unduly high or low flow velocities. Pipelines shall be designed for normal flow velocities at peak periods within the range of 0.5 to 2.0 m/s.

For pumping mains an economic appraisal may be required to determine the most economical diameter of pumping main to minimise the combined capital and discounted pumping cost. The resulting velocity will normally lie in the range 0.8 m/s to 3.0 m/s. All booster pump station proposals (including fire pumps) and design considerations should be consulted with the WSE in the first instance.

The following factors shall be considered in determining flow velocity:

- Avoid stagnation

Minimise turbidity (large fluctuations in flow rates can dislodge the biological slime or stir up settled solids in pipelines)

Pressure

Surge

Pumping facilities

Pressure reducing devices

Pipe lining materials.

Quick-closing valves, pumps, hydraulically driven equipment or any other equipment which may cause pressure surges or fluctuations to be transmitted within the water supply system, or compromise the ability of the WSE to maintain its stated levels of service, shall not be used on any piping beyond the point of supply. In special circumstances such equipment may be approved by the WSE.

## DESIGN PRESSURES

The design pressures are the limiting pressures for operation of a water supply system including any allowance for variation of usage in the future. Minimum and maximum design pressures shall comply with Section 2.5.3.1. Design pressures are set at the water meter. Specific consideration should be given for multi-storeyed buildings or areas of significant contours.

The operating pressure shall not exceed the re-rated pressure class/rating or the operating pressure limit of the pipeline components at that location.

Design criteria for pressure should include those factors discussed in sections 4.1.5 and 7.3.

## PRESSURE CLASS OF SYSTEM COMPONENTS

### Reticulation systems

WSEs shall state the minimum pressure class of all pipe materials. Where the WSE has no requirement the minimum pressure rating of PN12 shall be used for all pipe material and PN16 for all components. Refer also to the WSE's approved products/materials registers.

### Systems subjected to dynamic pressures

Pressures shall be modelled in systems subjected to dynamic pressures. Where modelling shows pressure spikes in the range of 90-120m the minimum pressure rating shall be PN16 for all pipe material and components.   Where pressure spikes in excess of 120m are shown the design shall be modified to eliminate pressure spikes.

## THRUST AND ANCHOR BLOCK DESIGN

Thrust blocks and any other pipe restraint system shall be designed to resist the test pressure.  Refer to Section 7.9.2.

## SYSTEM TEST PRESSURE

The hydrostatic test pressure at any point in the pipeline shall be:

- Greater than the design operating pressure

Less than or equal to 1.25 times the rated pressure of any pipeline component.

Note: The design pressure is the maximum system pressure at a point in the pipeline, considering future developments, static pressure, dynamic pressure and an allowance for short-term surge pressure (water hammer), as determined by analysis.  Refer to Section 19.4 for hydrostatic pressure testing requirements.

## DESIGN FOR DYNAMIC STRESSES

A surge analysis shall be undertaken for any pipeline within a pumped system or system containing automated valves. The source of any significant pressure surges or high-pressure areas shall be identified and remedial measures to minimise pressure surges designed and specified.

### Fatigue

Although plastic pipes may be permitted in zones affected by dynamic pressure variations (e.g., pump zones), in locations downstream of pressure reducing valves, and in high surge areas, it is essential that the pipe class be reclassified (re-rated) for both surge and fatigue (cyclic dynamic pressure variations) in accordance with the criteria set out in Polyethylene Pressure Pipes Design for Dynamic Stresses, PIPA or PVC Pressure Pipes Design for Dynamic Stresses, Refer to POP 010A POP 010B and POP101.

Prior to plastic components being specified for mains in a pumped system, or a system otherwise exposed to regular surge / water hammer, the Designer shall verify suitability by applying the relevant design assessment nominated in Table 3-5.

| Table 3-5 - Methods for Design of Plastics Pipes and Fittings for Dynamic Stresses |  |
| --- | --- |
| Pipeline system items | Guideline |
| PVC pressure pipes | PIPA Guideline POP101: PVC pressure pipes—Design for dynamic stresses. NOTE: where fittings are required for PVC pipelines, they shall be ductile iron |
| PE pressure pipes | PIPA Guideline POP010A: Polyethylene pressure pipes—Design for dynamic stresses |
| PE fusion fittings | PIPA Guideline POP010B: Fusion fittings for use with polyethylene pressure pipes—Design for dynamic stresses |
| GRP pipes and fittings | There is limited data to detail the design of GRP pipes and fittings and their performance. Systemic fatigue is dependent on the integrity of the manufacturing process, particularly for fittings. Fatigue design of GRP pipes and fittings requires WSE authorisation with appropriate specialist input. The design must be objectively certified with reference to testing and validation of criteria documented by the manufacturer. Specification of ductile iron fittings in lieu of GRP fittings should be considered for applications subjected to significant fatigue loadings. |

## TEMPERATURE DE-RATING OF PLASTICS PIPES AND FITTINGS

The pressure class of plastics pipes is determined at 20°C. Where the time weighted 12-month average temperature of water within the distribution system exceeds 20°C, the pipe class shall be de-rated to the time weighted 12-month average temperature. The temperature de-rating factor, t, shall be in accordance with Table 3-6.

| Table 3-6 - Temperature De-Rating Factors for Plastics Pipes Operating at Elevated Temperatures |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Pipe material | De-rating factor1, t |  |  |  |  |
|  | Time weighted 12-month average temperature, °C |  |  |  |  |
|  | 20 | 25 | 30 | 35 | 40 |
| PVC-U5 | 1.0 | 0.94 | 0.87 | 0.78 | 0.70 |
| PVC-M5 | 1.0 | 0.94 | 0.87 | 0.78 | 0.70 |
| PVC-O5 | 1.0 | 0.94 | 0.87 | 0.78 | 0.70 |
| PE 80B2 | 1.0 | 1.0 | 0.83 | 0.77 | 0.77 |
| PE 1002 | 1.0 | 0.91 | 0.91 | 0.83 | 0.83 |
| GRP4 | 1.0 | 1.0 | 1.0 | 1.0 | 1.0 |
| Notes 1) At elevated temperatures, a reduction in the design life may occur. 2) The figures for PE80B and PE100 are based on PIPA POP013 Temperature rerating of PE pipelines. The guidance provided in POP013 is based on typical PE compounds used in Australia and New Zealand to manufacture AS/NZS 4130 PE pipe and listed in PIPA Guideline POP004 Polyethylene Pipe Compounds. 3) Multiply the temperature de-rating factor t by the PN number of the pipe to determine the de-rated PN of the pipe. 4) The figures for GRP are based on a polyester body resin. However, for continuous operation ≥35°C vinylester resins are required. No temperature de-rating is required up to 50°C for GRP pipes with vinylester body resins. 5) The figures for PVC pipe re-rating are based on PIPA "Temperature Derating of PVC Pipes for Pressure Applications" (TN003) and "PVC Pressure Pipes Design for Dynamic Stresses" (POP101). |  |  |  |  |  |

## DE-RATING OF MANUFACTURED PE COMPONENTS

Where components are formed from cutting and welding polyethylene (PE) pipe the original pressure class of the pipe shall be decreased following the processes in AS/NZS4129.

The minimum pressure class (PN) of pipeline components shall be:

- Gravity and pumped systems comprising metallic components:

PNMin ≥Design Pressure (MPa)

Gravity reticulation systems incorporating plastics components:

PNMin ≥Design Pressure (MPa) x (1/t)

Systems exposed to systematic surges and incorporating plastics components:

PNMin ≥PN de-rated for fatigue as per Section 3.6 and

PNMin ≥Design Pressure (MPa) X (1/t)

where t = temperature de-rating factor for plastics components

Notes

- Plastics-bodied fittings and valves present a special problem. The geometry of these items can result in complex stress patterns that 'amplify' the apparent stress cycle. An apparently harmless pressure cycle can thus produce a damaging stress cycle leading to a shortened fatigue life. This is particularly important in the case of branch fittings such as tees. In addition, the situation can be aggravated further by the existence of stresses from other sources, for example, bending stresses induced by flexing under hydraulic thrust in improperly supported systems.

- The design of plastics-bodied fittings and valves is not standardised. The manufacturer should be consulted for re-rating factors for cyclic loading conditions, and, irrespective of manufacturer's advice, shall be not less than the values given in PIPA guideline documents referenced in Table 3-6.

- The pressure range is defined as the maximum pressure minus the minimum pressure, including all transients, experienced by the system during normal operations. The effect of accidental conditions such as power failure may be excluded.

# PRODUCTS AND MATERIALS

## GENERAL

All Products and Materials used in any Water Supply reticulation system must comply with the WSE’s Approved Products and Materials lists which are available from the WSE.

All parts of the water supply system in contact with drinking water shall be designed and constructed using components and materials that comply with AS/NZS 4020 (Revised 2018).

### Pipe selection

The selection of the appropriate pipe material, sizes, and pressure classes shall be based on system demands. See Section 3.3 for the WSE’s minimum pipe pressure ratings.

### Standard pipe sizes

The minimum pipe sizes shall be standardised as per section 3.1.2 above

### Minimum pipe sizes

### Pipe PN class (pressure rating)

Pipe PN class is selected on the basis of the design pressure (head) calculated for the various sections of the reticulation network. This may be varied by specific operational requirements specified by the WSE. The minimum pipe pressure rating shall be PN12 (refer 3.3 and 4.1.6).

### Design pressure

The design pressure (head) for the mains to be installed shall be based on the following:

Design pressure, (m) = Maximum Supply Pressure, (m above the level datum used for the ground level)

+ Surge Allowance, (m)

– Lowest Ground Level (GL) of the proposed main, (m above datum).

The design pressure (m head) shall be used for:

- Selection of pipe materials and classes

Selection of pipe fitting types and classes.

### Minimum pipe PN

The minimum pressure rating for pipe shall be PN12 and for fittings PN16 on water reticulation mains. For some pipe materials the Entity will require greater minimum pressure class. Designers shall verify the WSE’s minimum requirement before specifying the required pipe PN. Refer to the WSE’s material supply standard.

Where pipes are installed using trenchless methods such as horizontal directional drilling, the minimum pipe class shall be PN16.

### Nominated pipe PN

In some cases, the WSE may nominate a pipe PN (such as PN 16) for pressure pipes and fittings to standardise on a limited number of pipe PNs, or to allow future operational flexibility within the system. Where this is the case, the design pressure used as the basis for system design shall not exceed the WSE’s specified operating pressure limit associated with the designated pipe PN.

### Pumped mains

When booster pump stations are considered, the requirements shall be reviewed with the WSE as they are not in the scope of this NEDS.

However for all water mains in pumped systems, a detailed surge analysis shall be conducted unless otherwise directed by the WSE to ensure:

- The appropriate surge pressure is included in the calculated design head

Surge control devices are included in the system design, where identified by the detailed analysis, to protect the network or control pressure fluctuations in the supply to customers, or both.

### Pipe materials

For acceptable pipe materials and Standards see the WSE’s material supply standards.

### Steel mains considerations

Internal and external corrosion protection should be discussed with the WSE.  Internal lining must conform with AS/NZS 4020.  Special coating systems are required for above ground installations including interface with buried sections.  Where Cathodic protection systems are recommended by the designer they must be discussed with the WSE early, as they require ongoing monitoring, therefore suitable arrangements for test points need to be considered.

## PROTECTION AGAINST DEGRADATION

### Protection against contaminated ground

Avoid contaminated sites wherever possible. The designer shall check land use history, particularly in brownfield areas or when development land has previously been zoned as industrial/commercial where fuel storage facilities may have been present.  If a contaminated site cannot be avoided, provide details in the Design Report covering  the requirements detailed in clause 5.4.6 of this NEDS as a minimum.

### Bolted connections

All buried bolted connections shall be wrapped in denso tape in accordance with manufacturer’s instructions.  All bolted connections shall be made with flanges. The WSE shall specify flange patterns for each network. Where no flange pattern is specified, flanges shall comply with AS/NZS 4087 PN16.

Note: AS/NZS 4087 has superseded AS 2129, AS/NZS 4087 PN16 corresponds to AS 2129 Table C and Table D.

# GENERAL DESIGN

## GENERAL REQUIREMENTS

Alteration to existing infrastructure
The connection of new developments may require upgrading or extending the existing water network and must maintain the minimum level of service for the existing infrastructure. Alterations to the existing water network to achieve the required level of service and standards for development outside of the on-demand water supply areas, the water supply area or restricted flow area must be at no cost to the WSE.

### Design tolerances

The location and levels, where applicable, of the water main shall be determined and specified to the following tolerances:

- Horizontal alignment in metres to one decimal place for all mains.

Level:

- Reticulation mains, to meet minimum cover requirements.

- Transfer and reticulation mains, in metres to two decimal places

Horizontal alignment shall be referenced to the WSE’s preferred coordinate system, and where possible, to local property boundaries. Levels shall be referenced to NZVD2016 or other as required by the WSE.

### Levels

Levels are to be provided in the design drawings for any road crossings and other service crossings, valves adjacent to road crossings, changes of grade and at intervals on vertical curves to ensure minimum and maximum cover levels are met.

### Water main renewals electrical safety and earthing to water services

Properties have a variety of electrical earthing arrangements that can involve the water supply system. These range from use of the metallic water service as the main earthing conductor (in some areas with older reticulation systems) to provision of an equipotential bond between the electrical main neutral and the water service (in conjunction with an earth stake in compliance with the Wiring Rules (AS/NZS 3000). Each of these arrangements, whilst designed to protect occupants, can create dangerous electrical conditions on the water supply pipework when there is a defect in the property electrical installation or the electricity supply network.

Appropriate safety warnings shall be included in the Specification and/ or Design Drawings commensurate with the safety precautions developed.  For example, a typical warning consistent with the method outlined above could be:

Where a metallic water main is to be replaced using plastics pipes, the electricity supplier or a licensed electrician shall assess affected properties' electricity supply for defects and the likely effect on earthing adequacy. Work can commence once the electricity supplier/electrician declares in writing that it is safe to proceed.

### Survey Control

#### Marking

All survey work submitted to the WSE shall be directly related to the WSE’s coordinate system. The plan shall clearly identify the origin of both horizontal and vertical control and shall quote the values adopted in each case.

#### Horizontal control

Control marks of engineering and cadastral survey standard will normally be sufficient for positioning of pipelines and associated facilities. Data supplied to the WSE shall include coordinates for all control marks used or placed during the survey.

#### Vertical control

Sufficient level control marks shall be provided to satisfy construction requirements.

Marks shall be positioned in locations that are stable and unlikely to be disturbed by construction. Marks shall be spaced to minimise set-ups needed when pegs are replaced or Work As Built levels are run after construction.

The surveyor shall verify levels at every opportunity by connecting to other control marks.

## RETICULATION DESIGN FOR WATER QUALITY

### Layout of water mains

In determining the general layout of mains, the following factors shall be considered:

- Main location to allow easy access for repairs and maintenance

Whether system security, maintenance of water quality, and ability to clean mains meet operational requirements

Safe location of valves for shut-off areas and zone boundaries (see 5.6.2.1)

Safe and easy access to fire hydrants for maintenance and FENZ in an emergency

Avoidance of dead ends by use of looped mains or rider mains

Provision of dual or alternate feeds to ensure a resilient supply

In brownfield situations consider the location and alignment of other buried or underground services

Consider material type and evidence of engineering evaluation, i.e., location to fuel stations; and

Compatibility with the WSE’s long term management strategy and plan for the overall district zone.

Network layouts shall be established in accordance with the WSE’s requirements to provide security of supply and zone management, and interconnected ring systems. Any design should demonstrate a consideration for security of supply. Typical examples of suitable layouts are given in Drawings WS-02 Intersection Layout and WS-03 Looped and Link Mains.

### Looped mains

#### Water age

Drinking water supply systems shall be designed to minimise water age to ensure no unacceptable deterioration of water quality. This shall include:

- Mains with dead ends (or termination points (see 5.2.2.2) shall be avoided by the provision of looped watermains. Particular care shall be taken at the boundaries between supply zones where dead ends shall be avoided or minimised whilst maintaining existing district zone boundaries.

Mains for short runs shall be reduced in size or looped, for example no-exit roads (see Figure 5-6)

The WSE may at its discretion require the developer to implement a system to improve the water quality where development uptake versus overall size affects the water quality of the area. This may be in the form of temporary dosing systems and flushing. A development staging strategy shall be provided to the WSE with commitment to provide for any associated costs before connecting to the WSE system.

#### Termination points

Termination points or dead ends should be avoided to prevent poor water quality. Alternatives such as a continuous network, link mains, rider mains, looped mains, installation of flushing points on rider mains at dead ends and the use of reticulation mains smaller than DN100, particularly in no-exit roads, should be considered (see Figure 5-5 and Figure 5-6), all subject to meeting fire fighting requirements.

### Link mains

A link main (See Figure 5-6) is an alternative means of eliminating a dead-end in situations where a looped main is not feasible. A "link" may be achieved by laying a main between the court bowl or cul-de-sac and a main in an adjacent street, via a pathway or right of way. The link main shall be the same size as the smaller of the two mains being linked.

### Reduced size mains

These are generally not allowed.  Under circumstances where there would be water quality improvements by using a reduced size of main, i.e., a dead end or firefighting capability of any proposal must be proven to the WSE and FENZ.

## WATER MAIN ACCESS

Water mains in private property

Water mains shall only be installed in the public road reserve. Public water mains in private property, right of ways (ROW) and private roads are not permitted without consultation and agreement with the WSE and provision of acceptable access over the main for replacement, operation and maintenance.

## LOCATION OF WATER MAINS

### General

Water mains shall be located in the road reserve and follow guidance given in the National Code of Practice for Utility Operator’s Access to Transport Corridors, Version 2, July 2019 by NZUAG.  The location shall be specified by the Council or WSE, within the road reserve or space allocation nominated by the Road Controlling Authority. Where approved by the Council or WSE, water mains may be located in a public reserve or park. In some instances, an easement may be required depending on the discretion of the Parks Manager.

Water mains shall:

- Be aligned parallel to property boundaries, and typically located in the berm

Not traverse steep gradients, if unavoidable, add bulkheads to the design refer clause 7.10

Be located to maintain adequate clearance from structures and other infrastructure. Refer Section 10.13.

A typical cross section layout for public roads is provided below in Figure 5-1.

Figure 5-1- Typical cross section layout for public roads

### Water mains in road reserves

The location of assets in the road corridor shall meet the requirements of the whole of Section 5 of this NEDS and satisfy the Road Controlling Authority’s particular requirements.

### Location in other than public road reserves

A WSE’s water mains shall not generally be located in private property.  In exceptional circumstances a WSE may allow it only if an appropriately sized and registered easement is provided in accordance with the Territorial Authority’s and its own rules.

### Effect on vegetation

If installation is required under existing trees and vegetation, then trenchless technology should be considered. If this is not practicable, advice from a qualified arborist is required to minimise damage to the vegetation.
No works are to commence within 30m of historic/protected or notable trees without written approval from Council parks staff and if in a road corridor the road controlling authority. The road controlling authority or Council may require that an arborist monitor works in or around these trees.  Note: Notable Trees are recorded in district plans prepared under the RMA. Other council policies manage street trees and reserves under the Local Government Act and Reserves Act respectively

### Water mains near trees

Locating water mains within the root zone of trees is not allowed.

### Contaminated sites

Contaminated sites should be avoided. Where a contaminated site has been confirmed, written approval to proceed shall be obtained from the relevant Council and the WSE. The following issues shall be addressed in the request for approval:

- The nature of the contamination

Compliance with statutory requirements

Options to decontaminate the area

Selection of appropriate pipe materials, coatings and jointing techniques to maintain water quality

Selection of pipeline materials to achieve the required life expectancy of the water main

Safety of construction and maintenance personnel

Special water main maintenance considerations to protect personnel and water quality.

Water mains and connections in the immediate vicinity of petrol stations shall not be constructed of PE or PVC material  . Instead the designer shall consider using Ductile iron mains with nitrile rubber ring and gaskets. PE-Al-PE barrier pipe submains, crossovers and laterals shall be installed outside of bulk fuel storage facilities including petrol stations. Length of installation shall include the entire length of the property boundary plus extending a minimum of an additional 15 m on each side.

Any contaminants in the soil, including topsoil on the site, shall be at the lesser levels of the health-based or environmental-related protection values as described below:

- Health-based protection values:

NES Soil contaminant standards (SCS) for residential land use (no produce, if applicable) as derived in accordance with Ministry for the Environment Methodology for Deriving Standards for Contaminants in Soil to Protect Human Health (Chapter 7). In the absence of a derived NES Soil SCS, then a standard following the hierarchy outlined in the Ministry for the Environment, Contaminated Land Management Guidelines No 2 shall be adopted. Environmental-related protection values:

No free (or separate) phase liquid contaminants and groundwater contaminant concentrations, with the exception of volatile organic compounds, which must be below the Australian and New Zealand Guidelines for Fresh and Marine Water Quality at the level of protection for 80% of freshwater species. Concentrations of volatile organic compounds shall be below typical laboratory screening detection limits (0.5 mg/L or lower).

The following table sets out the acceptance criteria for contaminant free sites:

| Table 5-1 – Acceptance criteria for contaminant free sites |  |
| --- | --- |
| Contaminant | Acceptance level (mg/kg) |
| Arsenic | <24 |
| Cadmium | <7.5 |
| Chromium | <400 |
| Copper | <325 |
| Lead | <250 |
| Mercury | <0.75 |
| Nickel | <1051 |
| Zinc | <2001 |
| Benzo(a)pyrene equivalent | <2.15 |
| Pyrene | <1 |
| Total DDT | <0.7 |
| VOCs | Below laboratory detection limit |

1 Can use upper limit background concentration in Auckland region (i.e., 320 for Nickel and 1160 for Zinc) if the soil is volcanic source

A site investigation including soil sampling and testing must be undertaken and a report submitted to the WSE in accordance with the requirements of the Ministry for the Environment 2011 Contaminated Land Management Guidelines No. 1 - Reporting on Contaminated Sites in New Zealand. Testing shall be conducted by a NATA/IANZ accredited laboratory.

Soil testing data is required at the position for the proposed water infrastructure. The WSE reserves the right to request additional soil testing at the cost of the developer where the data supplied is considered inadequate or not representative of the site.

### Safety in Design

For all designs, but especially those in contaminated ground, a full Safety in Design workshop must be carried out and fully recorded in a register.  Any issues raised shall be carried through and dealt with in detailed design and/or construction.

### Location markers

The location marking of valves and fire hydrants shall be to SNZ PAS 4509 and as shown on the standard drawings  WS-05.

### Marking tape

Appropriate marking tape or detection tape shall be installed at the top of the embedment zone, or tied to the pipe during horizontal directional drilling, to aid in the future location of the pipe. Refer to AS/NZS 2032 section 5.3.15.

## CROSSINGS

### Location of water mains on bridges

The pipe bridge must not be integrated with the bridge support structure. The design must provide for safe and unrestricted access for maintenance, upgrade, or replacement. The pipe shall be positioned clear of the 1% Annual Exceedance Probability (AEP) flood levels. The pipe and supports shall be structurally designed to meet the following conditions (refer Section 7):

- Empty and full static loads

Any dynamic loads and vibration

Expansion and contraction

Seismic action.

Timber supports are unacceptable. Provision shall be made for access and clearances to maintain the pipe, connecting structures, drainage, articulation joints, valves, and associated fittings as necessary.

Unauthorised bridge access (i.e., onto the pipe) shall be prevented with an adequate barrier structure and, if necessary, on-bridge railing for fall protection.

The following pipe material options can be considered:

- Polyethylene pipe: This material must be butt welded and supported inside a full-length carrier pipe of suitable rigidity and durability. Cradles are not acceptable. The carrier pipe must be of suitable internal diameter to allow for future pipe size upgrades and thermal expansion and contraction.

Steel (lined mild steel or stainless steel): The joints must be welded or flanged. Pipe hangers or supports should be fully welded to reduce corrosion and simplify maintenance

Ductile iron with flanged joints with hangers or supports that prevent galvanic corrosion and encourage water run-off.

A formal agreement with the bridge owner must provide the WSE with the ability to access, operate and maintain the pipe on the bridge. NZTA Bridge Manual SP/M/022 gives guidance on placement of utilities in cavities on new and existing bridges.

### Crossings

#### General

Water main crossings of roads, railway lines, and underground services shall be at right angles. Ducting and additional protection of the crossing service is subject to the affected authority’s requirements. In any event, the water main crossing shall be sized at minimum 100 NB unless otherwise instructed by the WSE. Mains should be located and designed to minimise maintenance and crossing restoration. The WSE may require extra mechanical protection for the pipes or different pipe materials to minimise the need for future maintenance.

#### Railway reserves

Water mains shall not be laid within railway reserves unless it is absolutely necessary, in which case the crossing shall be designed to the railway owners requirements and be authorised in writing by the railway owner.

#### Crossings of waterways or drainage reserves

All crossings of waterways or reserves shall be specific designs to suit the WSE's requirements and be in accordance with the Regional/Unitary Authority rules and policies.

Crossings shall be sized according to the hydraulic requirements and any WSE applied requirements for minimum diameter for future proofing. and as far as practicable, be at right angles to the waterway or reserve. Crossings shall be below waterway invert unless it can be demonstrated that such a crossing is not practicable.

When the pipeline is placed under the invert level of a waterway it may require mechanical protection by concrete encasement or steel or other acceptable pipe duct. Different pipeline materials may need to be used for the crossing.

#### Overhead power lines and transmission towers

Water mains constructed from metallic materials shall generally not be located close to high voltage transmission lines and other facilities. Special design shall be undertaken if it is necessary to locate water mains close to such facilities.

For any situation where a metallic pipeline is located in proximity of electrical transmission lines, particular attention is drawn to AS/NZS 4853 Electrical hazards on metallic pipelines. Similarly, A Guide to Power System Earthing Practice published by the Electrical Engineers Association is a useful reference (www.eea.co.nz)

## VALVES

### Valves general

Valves shall be installed to permit isolation of sections of the pipe network for maintenance and operational purposes. The spacing and location of valves shall be such that:

- the number of properties (or equivalent population in areas of multi-unit type apartments) affected by a shutdown is no more than 50

maximum spacing of 500m

Valves shall be provided:

- Following the typical arrangements shown in drawings WS-02 and WS-03

- Anti-clockwise closing (with the exception of small diameter gate valves or peet valves)

- Both sides of crossings for motorways, arterial roads, and railway and tram crossings

Adjacent to street intersections (for ease of location)

At least 2 valves at every tee

In the footpath, clear of carriageway, where possible

Within 50 m of a bridge abutment, where distribution mains pass through motorway or arterial road bridge

Valves shall be flanged jointed and fully supported. No loads shall be passed onto the pipe

Valves and valve box lids shall be suitably marked and painted as follows:

- Hydrants – yellow

Isolation valves (typically open) – white

District zone valves (normally shut) – red

### Valving design

#### Valve siting principles

The siting of valves shall take a holistic view of the existing infrastructure and proposed additions. General principles to be considered shall include:

- Valves shall be sited to provide the control (such as flow, pressure, isolation, and diversion) required by the WSE

Ready access to valves to enable their safe operation. Account shall be taken of traffic and other site constraints

Minimisation of inconvenience to the public and avoiding clustering of surface fittings in the footpath at intersections

Optimisation of the number and location of valves to meet the WSE’s operation and maintenance requirements, safe working, and to minimise the effect of a shutdown on the WSE’s customers.

#### Valve spacing criteria

Valves to be spaced up to 500m or service up to 50 properties - whichever is less.

#### Branch mains

Valves shall be located on branch mains adjacent to the through water main. See Figure 5-2.

Where a road crossing is necessary immediately after the tee branch and there is no space available adjacent to the tee, a  valve shall be installed on the opposite side of the road.

Figure 5-2 - Branch valve adjacent to main

#### District Zone Valves

District zone boundary valves and hydrants shall be in a paired configuration with a standard fire hydrant located between them. See Figure 5-3. Installation in this manner permits the valves to be checked for leakage. The valve on the low pressure side of the pair will normally be closed in order for the fire hydrant to be used for firefighting purposes with the supply from the higher pressure zone.

District zone boundary valves on rider mains shall be subject to specific design in consultation with the WSE to identify operational requirements.

Figure 5-3 - Valve and hydrant combination for district zone dividing values.

The closed valve box shall be foamed to prevent accidental operation and the lid painted red. Kerb marking shall also be red to indicate the normally closed valve.

#### Secure service connections

Additional valves may be required at a service connection to customers needing greater security of supply such as hospitals and large industrial or commercial developments. Figure 5-4 illustrates typical arrangements to facilitate partial isolation of the main while maintaining supply to the customer.

Figure 5-4 - Secure connection

#### Valve siting principles

##### Gate valves and sluice valves

- Resilient seated Gate (isolation) valves (also known as Sluice valves) shall be anti-clockwise closing with a false dolly attached and shall be installed on principal mains

Gate valves (also referred to as peet valves) shall be clockwise closing and shall be installed on rider mains.

Valves shall include a label/tag confirming closing direction.

Buried valves shall be operated from above ground and shall be designed to facilitate the use of a standard key and bar. An extension spindle shall be incorporated as necessary to ensure the top of the spindle is reachable within 500mm, but not be sited less than 100mm from the finished surface level. In-line valves shall be the same diameter as the reticulation main.

##### Butterfly valves

Butterfly valves shall only be used with the approval of the WSE

### Pressure reducing valves (PRV)

Pressure reducing valves (PRV) are outside the scope of this NEDS. Refer to the WSE for requirements and specification.

A PRV is used to reduce the pressure to a desired lower pressure downstream of the valve. The PRV works automatically to maintain the desired downstream pressure. The WSE may require the PRV site to be monitored or controlled through its telemetry system.

### Pressure relief valves (PRelV)

Pressure relief valves (PReIV) are outside the scope of this NEDS. Refer to the WSE for requirements and specification.

### Pump control valves

Pumping is outside the scope of this NEDS. Refer to the WSE for requirements and specification.

### Pressure sustaining valves (PSV)

Pressure sustaining valves (PSV) are outside the scope of this NEDS. Refer to the WSE for requirements and specification.

### Air valves (AV)

The scope of this NEDS is limited to reticulation up to 300mm diameter.  The WSE should be consulted outside of urban areas for the requirements for ARVs and scour locations.

#### Installation design criteria

In densely populated urban environments with many service connections an air valve is often not required on a water reticulation main, and hydrants may be positioned at the high points to allow air release during drawdown and filling.  However, investigation into the need for air valves (AVs) shall be made for all high points on mains, particularly at points more than 2 m higher than the lower end of the section of water main and particularly if the main has a steep downward slope on the downstream side.

Where the hydraulic head is less than 10m, special consideration shall be given to the type of AV to prevent water leakage from the valve. AVs shall be installed with an isolating valve to permit servicing or replacement without having to shut down the main.

Combination AVs, that is (dual) AVs incorporating an AV (large orifice) and an air release valve (small orifice) in a single unit, are generally the preferred type for distribution and transfer mains, and where required on reticulation mains.

Watermains with only a few service connections or a configuration that leads to air accumulation may require combination air valves to automatically remove accumulated air that may otherwise cause operational problems in the water system.

The configuration of the distribution network for both the change in elevation and the slope of the water main govern the number and location of air valves required.

#### Air valve location

Air valves shall not be located in major roadways or in areas subject to flooding or in areas of high ground water without specific design to prevent backflow contamination of supply. When required, air valves shall be located:

- At summits (significant high points)

At intervals of not more than 800 m on long horizontal, ascending, and descending sectors

On the downstream side of PRVs

On the downhill side of major isolating valves

At blank ends

Where the air valve is in a valve chamber, the design shall ensure adequate venting for effective operation and drainage to prevent backflow contamination.  Wherever possible the air valve intake should be above the 1% AEP event flood level.

### NON-RETURN VALVES

Non-Return Valves (NRV) are outside the scope of this NEDS. Refer to the WSE for requirements and specification.

### SCOURS AND PUMP-OUT BRANCHES

The scope of this NEDS is limited to reticulation up to 300mm diameter; therefore it is possible that scours may not be necessary.However, they may be still be required on smaller water supply schemes as well.  Refer to the relevant WSE for further guidance outside of urban areas.

There shall be adequate drainage facilities to receive the flow resulting from flushing and draining operations.  Some Regional Rules require mixing chambers or manholes for de-chlorination prior to release.  Discharge to wastewater reticulation systems may require a Trade Waste Permit.  Refer to the relevant WSE for further guidance on scour discharge requirements.

Scours and pump-out branches on significant mains are provided in the distribution network for maintenance purposes. They are designed to allow draining of water from the mains by gravity or use of a mobile pump. Hydrants are preferred for flushing and draining on watermains DN <250.

Scours and pump-out branches shall incorporate appropriate measures to prevent back-siphon into the water supply system, including provision for fitting of any necessary backflow prevention devices.

Scours shall:

- Drain the watermain by gravity or have provision for pump-out within a period of 1 hour, or both

Have a diffuser fitted at the discharge point if there is a likelihood of environmental or asset damage

Not be subject to inundation; and

Scour valve boxes shall be painted red.

#### Scour size

Scours shall be sized in accordance with Table 5-2.

| Table 5-2 – Minimum scour size |  |
| --- | --- |
| Main size DN | Scour size DN |
| DN ≤200 | 80 |
| 200< DN ≤300 | 100 |

#### Scour location

Scours shall be located at:

- Low points at the ends of watermains; and

Low points between in-line valves. Scours shall drain to a point where the discharge is readily visible to prevent the scour valve inadvertently being left open.

Typical discharge locations include:

- An approved pit that is to be pumped out each time the scour is operated (called a pump scour);

A kerb and channel;

An open-grated street drainage sump;

A natural water course (with energy dissipater).

Scours shall not:

- Cause damage when operated;

Discharge to closed stormwater structures;

Discharge across roadways;

Discharge to waterways, unless in compliance with the appropriate consent requirements.

## SWABBING POINTS

In reticulation swabs shall generally use hydrants.  Where swabbing points are required by the WSE the design shall ensure there is sufficient drainage to deal with the flow from the water main from the flushing operations.  Also refer to Part Two Construction, section 18 Swabbing.

## HYDRANTS

### Purposes

Hydrants are installed on reticulation mains for firefighting and operational purposes. Operational purposes include mains flushing, chlorination, to allow the escape of air during charging, act as an air intake when draining to prevent main collapse and the release of water during dewatering of the water main, where air valves and scours are not installed.

Refer to Section 2.6.2 for backflow prevention requirements and Section 5.15.3 for metering requirements of private fire supplies.

### Hydrant siting principles

#### Hydrants for firefighting

The spacing of hydrants for firefighting shall be in accordance with SNZ PAS 4509.

For road safety reasons, hydrants on State Highways shall be placed outside of the Waka Kotahi NZTA roadside clearance zone and within 2m of the road reserve boundary

#### Hydrant installation

Fire hydrants shall not be fitted to reticulation mains DN <100 or to transmission mains. For access and operational safety, fire hydrants shall not be located along a vehicle crossing. Where a new vehicle crossing is constructed over an existing hydrant, the hydrant shall be relocated outside the designation of the vehicle crossing.

#### Marking of fire hydrants

All hydrant boxes and markings shall be painted with yellow road marking paint.

For hydrants on or adjacent to sealed roads additional marking shall include:

- An isosceles triangle of solid colour with sides 600mm and base 450mm. The triangle shall be located on or near the centre of the carriageway, with the apex pointing towards the hydrant.

A sawcut H, 5 mm wide, 5 mm deep, cut into the kerb opposite the hydrant, with 300 mm of the kerb also marked with yellow road marking paint.

A circle 1.2m outside diameter and line width of 100mm around the hydrant box. The circle shall be provided in locations where there is a risk of vehicles parking over the hydrant (e.g. where the hydrant is within 2 m of the kerb or edge of the carriageway, or more if there is angle parking).

A blue raised reflective pavement markers may be installed where deemed suitable instead of b or c where required by FENZ or the WSE. The reflective markers shall be bi-directional and placed close to, and on the fire hydrant side of the centre of the roadway, near the base of the yellow triangle marked on the road.

Marking shall be either b or c, not both.  Marking d) will only be required in circumstances where neither b) nor c) are acceptable to FENZ or WSE.

For hydrants on or adjacent to unsealed roads with no kerb marking shall include:

- An NZTA Type C marker post, replacing the two yellow reflectors with blue and repeated on the reverse side. The post shall be located as for the standard edge marking posts in relation to the trafficable portion of the carriageway and in line with the fire hydrant.

#### Hydrant size

All hydrants shall be a minimum DN 100.

#### Hydrant spacing

Spacing shall not exceed 135m in residential areas and 90m in commercial and industrial areas whilst fulfilling all the other requirements contained in SNZ PAS 4509:2008. On dead end roads in industrial/commercial areas, clusters of hydrants may be required to achieve required firefighting flows.

#### Hydrant location

All hydrant locations shall fulfil all the requirements contained in SNZ PAS 4509:2008.

#### Hydrants for reticulation system operational requirements

Additional to firefighting requirements, hydrants shall be provided at:

- High points on reticulation mains to release air during charging, to allow air to enter the main when dewatering, and for manual release of any build-up of air, as required, where automatic combination air valves (AVs) are not installed;

Localised low points on watermains to drain the water main where scours are not installed.

Adequate drainage facilities shall be provided to receive the hydrant flows from dewatering and flushing operations.

Air valves are not normally required on reticulation mains in residential areas where the configuration of mains and service connections will usually eliminate small amounts of air accumulated during operation; hydrants should be placed as close as possible to stop valves and high points to facilitate maintenance activities such as cleaning of watermains.

#### Hydrants at ends of mains

If a scour is not provided, a hydrant shall be installed at the end of every main DN ≥100.

## DISINFECTION FACILITIES

### General

The disinfection of water mains is usually achieved by injecting a solution containing free chlorine into the water main while charging the main with water through an adjacent valve. The process also requires the discharge of water from the other end of the water main. Also refer to Part Two Construction Section 20 DISINFECTION.

## TRENCHLESS TECHNOLOGY

Trenchless technology can contribute significantly to the reduction of carbon in construction and disruption to communities and so should be considered as part of the planning and design of any new reticulation.

Trenchless technology may be appropriate for alignments passing through or under:

- Environmentally sensitive areas

Built-up or congested areas to minimise disruption and reinstatement

Railway and road crossings

Significant vegetation

Vehicle crossings

Pressure pipes used for trenchless installation shall have either heat fusion welded joints, or suitable mechanically restrained joints, specifically designed for trenchless application, which may include integral restraint seal systems, or  other WSE approved pipe jointing method.

The Designer’s project execution plan shall detail the pipe structural limitations for the intended construction method, the location of access pits and exit points and include a risk assessment to other services, abutting surface and underground structures.

Further information on trenchless technologies may be found in ‘Trenchless technology for installation of cables and pipelines’ (Stein), ‘Trenchless technology – Pipeline and utility design, construction, and renewal’ (Najafi), and ‘Guidelines for horizontal directional drilling, pipe bursting, micro-tunnelling and pipe jacking’ (Australasian Society for Trenchless Technology)

## SHARED TRENCHING

Where shared trenching is approved the pipe structural calculations shall consider the pipe structural impact and minimum clearances from other services. See Section 5.16.2.

## PRINCIPAL AND RIDER MAINS

### Principal and rider mains layout

| Table 5-3 - Principal and rider mains layout |  |
| --- | --- |
| Area | Configuration |
| General Residential (Outside of Tier 1) | Principal main on one side of the road and a ridermain on the other. |
| Tier 1 General Residential, Industrial, commercial, medium and high density residential*, arterial or dual carriageway streets | Principal main on both sides of the road. |
| All other areas | Principal main on both sides of the road. |

No service connections are allowed to trunk mains >DN250, in which case a principal or rider main is required in accordance with section 3.1.

To facilitate future development, water- mains shall be laid across the full road frontage of the site at the developer’s cost.

### Rider mains and duplicate principal mains

A rider main shall be laid along the road frontage of all lots not fronted by a principal main.

Duplicate principal mains are required to provide adequate fire protection in the following cases:

- Arterial roads or roads with a central dividing island

Roads with split elevation

Roads with rail or tram lines

Urban centres

Parallel to large distribution mains that are not available for service connections

Commercial and industrial areas

Where required by SNZ PAS 4509

High density residential areas

## CONNECTION OF NEW MAINS TO EXISTING MAINS

### General

In specifying connection detail the designer shall consider:

- Pipe materials, especially potential for corrosion;

Relative depth of mains;

Standard fittings;

Pipe restraint and anchorage;

Limitations on shutting down major mains to enable connections; and

Existing cathodic protection systems.

Connections from the end of an existing main shall be designed to address any differing requirements for the pipes being connected, particularly restraint, spigot/socket joint limitations, and corrosion protection. The Designer shall consider the potential for insufficiently restrained/ anchored stop valves near the connection.

All connections shall have a branch connection isolation valve. Hot tapping of watermains shall not be completed without the WSE’s approval.

All connections to the existing reticulation shall be made by the WSE or a WSE Approved Contractor and in accordance with the WSE’s processes. Should a bulk supply point (BSP) be required refer to the WSE for its specific design requirements.

Connection of watermains to the public system may only be made with demonstration of compliance with the WSE’s disinfection processes, or if not available Section 20 of this NEDS and all the testing requirements of the WSE’s construction standards or policies have been fulfilled.

## TERMINATION POINTS

### Permanent ends of water mains

Termination points or dead ends should be avoided to prevent poor water quality. Alternative configurations such as a continuous network, link mains, looped mains, and the use of reticulation mains smaller than DN150, particularly in no-exit roads, should be considered (see Figure 5-5, Figure 5-6 and Figure 5-7).

Figure 5-5 - Elimination of termination points

Figure 5-6 Looped principal mains

Rider mains (also known as submains in some areas), DN <100, may be used to supply the furthest properties beyond the water main. The DN 100 main shall be laid to a point where all properties are provided with the fire protection required by SNZ PAS 4509.

A method of flushing shall be provided at the end of the rider main and water main, which shall be suitably anchored. Refer Figure 5-7 for an example of a flushing point on a rider main.  There must also be a testable backflow prevention device fitted to the flushing valve.

Note – The gate valve shall be in a normally closed position in a red painted lockable valve box and kerb marking.

Figure 5-7 - Permanent end flushing point for rider mains

### Temporary ends of water mains

Water mains shall be laid to within 1 m of the boundary of a subdivision where the main is to be extended in the future.

Temporary dead-end mains shall terminate with a hydrant followed by a gate valve. These shall be part of the holistic layout design to avoid unnecessary fittings not required for operations or maintenance. The valve and hydrant shall be suitably anchored so that the future extension can be carried out without the need to disrupt services to existing customers.

Where a development is staged, mains shall be constructed to terminate approximately 2 m beyond the finished road construction to ensure that future construction does not cause disruption to finished installations.

### Flushing points

Any requirement for flushing points shall be imposed by the WSE for their operational requirements.  Often they may not be required, however scours and pump-out branches on significant mains may be provided in the distribution network for maintenance purposes. They are designed to allow draining of water from the mains by gravity or use of a mobile pump. Hydrants are preferred for flushing and draining on watermains DN <250.

Scours and pump-out branches shall incorporate appropriate backflow prevention measures commensurate with the level of risk to the drinking water supply (refer Section 2.6.2)..

There shall be adequate drainage facilities to receive the flow resulting from flushing and draining operations.

Scours shall:

- Be spaced and located to drain the watermain by gravity or have provision for pump-out within a period of 1 hour, or both

Have a diffuser fitted at the discharge point if there is a likelihood of environmental or asset damage

Not be subject to inundation; and

Scour valve boxes shall be painted red.

## PROPERTY SERVICES

### General

The general requirements for service connections are as follows:

- Property service connections shall have suitable backflow prevention installed. See Section 2.6.2.

The point of supply is as defined under Section 2.2.1 and WS-01.

Only one service connection from the public watermain is allowed per lot; and

Superlots with over 50 dwelling units where pipework will remain private should be fitted with a second service connection if practical, but should ensure sufficient fire flows are met, the supplies are fitted with backflow prevention, and that accurate metering over the range of flows is installed. The internal layout design should make provision for flexible system isolation. The 50 dwelling unit threshold is to support the WSE customer service in the event of water outages.

A second connection for larger lots is at the WSE’s discretion and should demonstrate:

- Zone classification is not affected

Service connections are not interconnected within the property

Isolation for maintenance and emergencies is not adversely affected

Mixed land use type may require that the service connection and backflow prevention be separately sized and metered between commercial and domestic use.

Multiple private connections to dwellings on a single property, or where a subdivision does not provide a dwelling with direct public road frontage, may be supplied through a single bulk site meter and backflow prevention under a body corporate (or similar legal instrument) arrangement or with a manifold meter bank arrangement associated with the property. Private connections are made downstream (property side) of  the bulk supply meter or manifold.

A meter bank shall not house more than six individual water meters. Where more than six individual meters are required for dwellings located along a right-of-way or private road, a bulk site meter installation and backflow prevention shall be used in conjunction with private check meters, and a body corporate (or similar legal instrument) arrangement.

Right-of-ways or private roads greater than 135m from the public watermain to the furthest dwelling must have a bulk site meter arrangement in conjunction with private check meters, and a body corporate (or similar legal instrument) arrangement.  Adequate fire protection in accordance with NZS 4509 will also be required.

### Multiple Dwellings

A property may have multiple dwellings, or separate living units constructed within dwellings. Metering is required to the individual separable unit. The single bulk site meter arrangement has a reduced maintenance obligation on individual housing units and should be managed through a body corporate (or similar legal instrument), or in the case of a multi-storey apartment building a building management arrangement. The WSE will provide service for separate meter readings and individual billing to customers.

### Service line connections

The service connection onto the water main is made with a tapping saddle.  Connection saddles, pipe and pipe fittings shall be as required by the WSE’s material supply standards.  The WSE may require the service line to be placed in duct if it is laid at depth or complying with local requirements. The property service lead shall be minimum 20NB. The standard sizes shall be 20mm, 25mm, 40mm, 50mm, 80mm, 100mm and 150mm

The service connection shall be tapped from the top of the water main, rising directly vertical to a minimum cover of 450mm. A 90ᵒ elbow shall be installed at the top of the vertical tapping and the lead graded to a cover of maximum 250mm at the meter box adjacent to the property boundary. Refer drawing WS-18

Where a service connection passes under a driveway or other hard services, it shall be installed through a duct of suitable strength to support the driveway loading

The isolation valves must be of an acceptable type. Quarter turn valves are generally not accepted for isolation

Manifolds must be to the WSE standard design or approved equivalent. See the NEDS’s drawing WS-18

#### Under pressure connections to PE mains

When the tapping is made onto a PE pipe the use of an electrofusion fitting is preferred, but compression fittings may be used if agreed with the Entity.

#### Fire suppression connections

All private fire supplies shall be metered. If serving a sprinkler system the meter shall not be mechanical. Also a backflow prevention device must be installed.  Fire suppression supplies must be sized and designed by a qualified Fire Engineer.

Whilst the WSE does not bill the customer on fire supplies, the purpose of a water meter is to identify leakage or unauthorised use of the fire supply water within the private property.

#### Metering

Applications for new water meters must be made to the WSE.

The WSE retains sole ownership of water meters and single bulk site meters at the point of supply and is responsible for the ongoing maintenance of associated fixtures and fittings.

The WSE is not responsible for any private check meters.

All new or redeveloped residential and non-residential units, whether individually titled or not, must have individual manifolds installed for each individually occupied unit or premises. Where the property is managed by a legal entity such as a body corporate a bulk site meter at the boundary is required.

Meters must be located in the road reserve next to the property boundary and be readily accessible at all times. Meters shall not be installed in confined spaces. Properties, such as in a CBD, where meters cannot be located within the road reserve must be approved by the WSE. The design shall take into consideration the following:

- The shortest possible pipe length inside the property and must be readily accessible for maintenance

Each meter must be readily accessible for reading, maintenance, or replacement (boxes need to be sized appropriately)

Meters must not be located inside actual units/apartments or within ceiling cavities

Integrated remote reading devices must be installed when a meter is located behind a door or gate (locked or unlocked), fence or within an area protected by security systems. The remote reading device must be easily accessible to a meter reader. The remote reading device must be compatible with the WSE devices.  Smart meters may be installed as an alternative if agreed with the WSE.

Meters, excluding private check meters shall only be installed by the WSE’s approved contractors in accordance with the WSE’s standard details.

Water meters shall comply with the requirements of the WSE’s material supply standard.

The meter size for the development will be determined by the WSE. In-line meter on fire supplies must be endorsed by the fire design engineer. Demand flow requirements must be provided when the water connection is applied for.

For separate fire suppression a water meter shall be installed (refer drawing WS-20).

For combined fire suppression and water meter supplies a meter shall be installed. Depending on the watermain size a bypass meter may be required for low flow accuracy. The WSE must have access to read this meter.

Domestic and commercial use within a property shall be separately metered. Metering shall be combined for fire suppression and commercial with a separately metered domestic supply.

Appropriate backflow prevention shall be installed for (c), (d), (e) and (f) above.

A customer may wish to attach logging or remote telemetry to a water meter to assess consumption patterns or manage resource use; where this is authorised by the WSE no liability will be taken if the meter is changed, or data is unavailable for any period of time.

The WSE reserves the right to manage connections to its assets and may require that privately owned equipment connected onto the meter be removed at any time.

#### Coupling to meters

- Fittings, couplings, and pipe componentry shall comply with the requirements of the WSE’s material supply standards and the arrangements as shown in the drawing set in Appendix A.

The minimum upstream and downstream connection clearances of the meter manufacturer shall be allowed for.

#### Private water supply pipes

The private internal plumbing system’s design, installation, and maintenance (both in its component parts and its entirety) must comply with the Building Act 2004 and the New Zealand Building Code

## OBSTRUCTIONS AND CLEARANCES

### Clearance from structures and property boundaries

Pipes in trenches adjacent to existing buildings and structures shall be located clear of the ‘zone of influence’ of the building foundations as shown in Figure 5-8.

Figure 5-8 - Pipe trench minimum distance from building foundation

If this is not possible, a specific design shall be undertaken to cover the following:

- Protection of the pipeline

- Long term maintenance access to the pipeline

- Protection of the existing structure or building

- Consideration to building overhangs and clearances

- Building over water mains is not permitted.

The protection shall be specified by the designer for evaluation and acceptance by the WSE. Table 5-4may be used as a guide for minimum clearances for access to watermains.

| Table 5-4 – Minimum clearance from outside edge of pipe to wall, building or property boundary |  |
| --- | --- |
| Pipe diameter DN | Clearance to wall or building (mm) |
| <100 | 600 |
| 100 – 150 | 1000 |
| 200 -250 | 1500 |
| Note: The minimum distance shall allow for future pipe repair and replacement without disturbance to any fence, wall or adjacent foundation, so shall vary with depth and WSE requirements |  |

### Underground obstructions and services

#### General

Water mains that are public and installed in the proximity of other services shall comply with the WSE's minimum clearance requirements. The specific design may require a greater clearance.

#### Clearance requirements

The minimum vertical and horizontal clearances are shown in Table 5-5

| Table 5-5 – Clearances between watermains and underground services |  |  |  |  |
| --- | --- | --- | --- | --- |
| Utility (Existing service) | Minimum horizontal clearance (mm) (Fig 5-8 ‘X’) |  |  | Minimum vertical clearance(1) (mm) (Fig 5-8 ‘Y’) |
|  | New main size |  |  |  |
|  | DN ≤250 | DN >250 |  |  |
| Water mains DN ≥ 600 | WSE may consider specific clearances for larger mains due to operational reasons. |  |  |  |
| Transmission water mains 600 > DN ≥375 | 600 |  |  | 500 |
| Water mains DN <375 | 300(2) |  |  | 150 |
| Gas mains | 300(2) |  |  | 150 |
| Telecommunications conduits and cables | 300(2) |  |  | 150 |
| Electricity conduits and cables | 500 |  |  | 225 |
| Wastewater and Stormwater pipes | 1000/600(4) |  |  | 500(3) |
| Kerbs | 150 |  |  | 600 |
| Notes: All clearances are measured as the inside open spacing between the external walls of services. 1) Vertical clearances apply when water mains cross another utility service, except in the case of wastewater when a vertical separation shall always be maintained, even when the main and wastewater pipes are parallel. The main should always be located above the wastewater pipe to minimise the possibility of backflow contamination in the event of a main break. 2) Clearances can be further reduced to 150 mm for lengths up to 2m when passing installations such as poles, pits, and small structures, providing the structure is not destabilised in the process or that the structural integrity of the trench is compromised. 3) Water mains shall always cross over wastewater and stormwater drains. 4) When the wastewater or storm water pipe is at the minimum vertical clearance below the water main (500 mm), maintain a minimum horizontal clearance of 1000 mm. This minimum horizontal clearance can be progressively reduced to 600 mm as the vertical clearance is increased to 750 mm. 5) Clearance from kerb and channel shall be measured from the nearest edge of the concrete. 6) Where a main crosses the other services, it shall cross at an angle as near as possible to 90% |  |  |  |  |

Figure 5-9 – Service clearance measurements

### Clearance from transmission towers

Water mains constructed from metallic materials shall generally not be located close to high voltage transmission lines and other facilities. Special design shall be undertaken if it is necessary to locate such mains close to such facilities.

For any situation where a metallic pipeline is in proximity of electrical transmission lines, particular attention is drawn to AS/NZS 4853 Electrical hazards on metallic pipelines. Similarly, A Guide to Power System Earthing Practice published by the Electrical Engineers Association is a useful reference (www.eea.co.nz)

### Deviation of water mains

#### General

Deviation of a pipeline around an obstruction can be achieved by deflection of the pipeline at joints, to the angular deflection limits stated by the pipe joint manufacturer and with suitably restrained fitting bends. Permitted angular deflection varies with pipe material, pipe wall thickness, pipe PN class, joint type, design, and geometry. Some joint types are specifically designed to accommodate angular deflection. PVC and PE pipes may also be curved along the pipe barrel, between joints, to a radius of curvature not less than that stated by the pipe manufacturer. Curved water mains require the WSE's approval and may not be allowed due to pipe joint stresses, performance in a seismic event or operational constraints.  POP202 – PVC and PE Pressure Pipe Installation on Curved Alignments give advice on this topic that the designer may consider.

# SYSTEM PRESSURE MANAGEMENT

## GENERAL

Water supply reticulation is generally planned and designed to use gravity to convey water, designed to provide for the customers' water demands within the pressure ranges shown in Table 2-5. However, where variations in topography limit the viability of a gravity system or where pressures fall outside the required pressure ranges, other means of ensuring appropriate pressures need to be employed.
If the minimum pressure is insufficient during delivery of diurnal and/or seasonal demands, in-line pressure booster pumping stations (hereinafter called "boosters") may be used to increase the hydraulic gradient to the areas that have inadequate pressure. The decision to construct a booster may also result from a requirement to supply water from a different supply zone or because of system head loss that prevents a section or sections of the network from sustaining the required minimum operating pressure.
Some WSEs may require the use of individual private booster arrangements which supply water at a single lot level in place of a booster for the entire water system. The installation, maintenance and power costs of these individual boosters are typically the responsibility of the individual lot Owner. The requirements for these types of private booster arrangements are provided by the local WSE and are not covered by this NEDS.
In some circumstances (see 6.4 Pressure Sustaining Valve Installations) a pressure sustaining valve installation may be used to limit the minimum pressure that is experienced in part of a water supply network. However, this might adversely impact downstream flows and pressures.
If the maximum pressure is of concern, pressure reducing valve (PRV) installations may be used to limit the pressure and/or control the range of pressures experienced.
Similarly, it may be necessary for privately owned PRVs to be installed on individual water services to limit the maximum pressure to that specified for some on-property plumbing fixtures.

## IN-LINE PRESSURE BOOSTER PUMPING STATIONS

Booster pumping stations require specific engineering design and are not therefore included in the scope of this NEDS.  However, the WSE’s design philosophy will:

- Clearly define the type of pump and pumping scenario in order to provide an optimal design for the system

That pumping systems meet the water peak demand, consented requirements or pre-determined rate as determined in consultation with Councils

Be based on peak hour demand e.g., PHD, when maximum storage is available

Be based on the consented rate or the supply source instantaneous flow rate available whichever is larger, for systems with no or minimal storage

Accommodate initial and future operating conditions.  Pumps should be specified to operate in the vicinity of their optimum efficiency points

Not negatively impact other water customers

## PRESSURE REDUCING VALVE INSTALLATIONS

Pressure reducing valves (PRV) are outside the scope of this NEDS. They require detailed engineering design and operational planning. Refer to the WSE for requirements and specification.

Where a development's water supply pipework cannot be designed to deliver below the maximum allowable supply pressure, or the range of supply pressure during the day is more than 40m, then the WSE should be consulted on the possibility of using a pressure management device.

A PRV is used to reduce the pressure to a desired lower pressure downstream of the valve. The PRV works automatically to maintain the desired downstream pressure. The WSE may require the PRV site to be monitored or controlled through its telemetry system.

## PRESSURE SUSTAINING VALVE INSTALLATIONS

Pressure sustaining valves (PSV) are outside the scope of this NEDS. They require detailed engineering design and operational planning.  Refer to the Entity for requirements and specification.

# STRUCTURAL DESIGN

## GENERAL

Seismic resilience of water infrastructure is vital to the communities they serve.  This section provides guidance to ensure continuous water supply after an event has occurred.

For installation conditions beyond those shown on the drawings, the pipeline installation, including non-pipeline elements such as pump station chambers, shall be specifically designed to resist structural failure. The design shall be in accordance with AS/NZS 2566.1 including the structural design commentary AS/NZS 2566.1 Supplement 1 and NZS 1170.5 including Supplement 1. Details of the final design requirements shall be shown on the drawings.

Pipe bridge design shall be subject to specific structural design of the pipe and supports for empty and full static loads, any dynamic loads, and full seismic provisions. Also see Section 5.5 Crossings.

## STRUCTURAL CONSIDERATIONS

Pipelines shall be designed to withstand all the forces and load combinations to which they may be exposed including internal forces, external forces, temperature effects, settlement, and combined stresses. The water main design shall include the selection of the pipeline material, the pipe pressure class, and selection of appropriate bedding material to suit site conditions. Consideration must be given to the future state or possible interactions with the trench that could affect the bedding material’s ability to continue functioning as designed, for example very fine self-compacting material may affect the cost of retaining the trench during replacement or other construction work near the trench.

## INTERNAL FORCES

Pipelines shall be designed for the range of expected pressures, including transient conditions (surge and fatigue) and maximum static head conditions. These criteria are discussed in sections 3.2 and 4.1.5.  In the case of transient conditions, the amplitude and frequency shall be estimated or modelled. The allowance for surge included in the maximum design pressure shall not be less than 20m. If any distribution mains are subject to negative pressure, they shall be designed to withstand a transient pressure of at least 8m below atmospheric pressure. A surge safety factor of 2 may be applied to the normal operating pressure to estimate the surge pressure in lieu of a detailed surge analysis.

## EXTERNAL FORCES

### General

The external forces to be taken into account shall include:

- Trench fill loadings (vertical and horizontal forces due to earth loadings);

Surcharge;

Groundwater, including the potential for floatation;

Dead weight of the pipe and the contained water;

Other forces arising during installation;

Traffic loads;

Temperature (expansion/contraction);

Seismic forces;

liquefaction forces.

The consequences of external forces on local supports of pipelines shall also be considered.

### Pipe cover

Pipeline cover shall be designed with depth to the top of the pipe measured to the final surface level:

- In berms a minimum cover of 600mm and up to a maximum of 1000mm

Where located in the front 1m width of the berm (next to the road surface) the minimum depth is 900mm

In carriageways a minimum 900mm up to a maximum of 1200mm; or

As otherwise agreed or required by the WSE and the Road Controlling Authority.

### Embedment zone dimensions

The designed trench width shall be the minimum width to allow pipes to be safely laid and all embedment material properly and sufficiently compacted.

### Trench width

Pipe trench width design shall be based on manufacturers recommedations or pipe structural calculations and shall maintain minimum clearances from other services. See 5.16.2.

### Buoyancy

The pipeline shall not be liable to buoyancy when empty and shall be designed with a factor of safety against flotation of 1.25.

## GEOTECHNICAL CONSIDERATIONS

### General

#### Geotechnical investigations

The Designer shall take into account any geotechnical requirements determined during the investigations for the development. All geotechnical log reports shall be uploaded to the New Zealand Geotechnical Database; https://www.nzgd.org.nz

Where required, standard special foundation conditions shall be referenced on the drawings.

Special design requirements may apply in any area susceptible to land instability or soil liquefaction. For indicative information refer to http://data.gns.cri.nz/geology.

Geo-professionals are to satisfy themselves of the correctness of the information and apply current knowledge when meeting any such special requirements.

#### Earthworks Geotechnical Information:

- In some instances the WSE may provide geotechnical site investigation reports or a geotechnical baseline report (GBR). This information shall not be considered as complete and shall be supplemented as necessary for the site specific activities.

All additional investigation locations shall be surveyed and immediately after the investigations are completed backfilled and sealed.

#### All additional geotechnical information obtained shall be uploaded to the relevant regional Geotechnical Database.Pipe selection for special conditions

Pipeline materials and jointing systems shall be selected and specified to ensure:

- Structural adequacy considering ground conditions and water temperature

Water quality, considering the chemical concentration and temperature of the water, the influence of applied stresses and lining material

Compatibility with aggressive or contaminated ground (consider HAIL sites)

Suitability for the geotechnical conditions

Compliance with the WSE’s requirements.

### Water mains in engineered or controlled fill

The designer shall take into account any geotechnical requirements determined during the investigations.

### Water mains in non-engineered fill

Water mains shall not be placed in non-engineered fill

### Construction of Water Mains in engineered fill

The designer shall take into account any geotechnical requirements determined during the investigations.

Where the route of a main requires filling or construction of an embankment (e.g., to achieve required lines, grades, and cross-sections), a geotechnical specialist shall investigate the site and design and supervise construction of the embankment, the trench and bedding for the pipeline. Relevant construction requirements shall be included in the Specification and/or Design Drawings.

## CONCRETE ENCASEMENT

### General

Where trenchless construction techniques are impractical (Refer to Section 5.10) and open trench construction methods are employed, concrete encasement shall be considered as an alternative embedment material where:

- There is a need to protect a main from external loading, typically where the main is laid in a major roadway or in a shallow trench

There is a need to reduce the need for future maintenance activity, where the main is deemed by the WSE to be inaccessible (e.g., laid in a major road, deep trench, under additional fill or other infrastructure)

The soil bearing capacity and trench foundation are inadequate

To resist flotation

The risk of erosion is high (such as through water courses).

Proposals for concrete encasement and/or any alternative options shall be subject to discussion with and approval by the WSE. Concrete encasement shall be structurally designed as a beam to withstand anticipated external loadings where the encased length of pipeline incorporates joints or the soil bearing strength is below 50 kPa.

When subjected to external loading (sometimes exacerbated due to greater rigidity), the pipe and encasement together are required to carry the imposed load. External loading may be due to heavy vehicle loading, construction in fill, different foundation materials, structures located over the main, etc.

Generally, the following types of pipe and fittings may be concrete encased:

- Welded steel pipe and fittings

Ductile iron, GRP and PVC pipe, subject to each encased length being designed as a beam and the termination arrangement of each end of the pipeline within the encasement being as approved by the WSE.

Welded PE pipe and fittings.

The following shall not be concrete encased:

Cast iron, wrought iron and AC pipes.

Flanged joints.

Sections of any main containing a service connection, hydrant, or valve (including air valves).

### Encased steel pipelines

All concrete encased steel pipe joints shall be fully welded i.e., plain ended with welded collar or butt welded and slip-in type welded joint. No service connections or off-takes shall be provided on the encased section of pipeline.

Steel pipelines to be concrete encased do not require external coating. Uncoated steel pipe that is to extend beyond the concrete encasement shall be fully protected using a Zn/Al metal spray coating and/or heat shrink polyethylene sleeving and/or an approved bitumastic tape wrapping system or other approved by the WSE. Protection shall extend from at least 150 mm within the concrete encasement to the position of full pipe protection beyond the encasement.

## WATER MAINS IN UNSTABLE GROUND

Wherever practicable, water mains shall be located outside the influence of a potentially unstable area. If it is not possible to do so, the Designer, jointly with the geotechnical specialist, shall take every action possible to remove, or at least minimise the potential for damage to a water main caused by movement of unstable ground.

## ABOVE-GROUND WATER MAINS

The design of above-ground water mains shall include the design of pipeline supports, maintenance and access requirements, control of unbalanced thrusts and pipe thermal movements, and shall address exposure conditions, such as corrosion protection, UV protection, freezing of watermains, and temperature de-rating effects on materials.

In such situations the pipe materials, support, and restraint for the pipes and fittings shall be detailed on the drawings.

Refer to Section 5.5 for other requirements.

## PIPELINE ANCHORAGE

### General

Anchorage shall be provided at bends, tees, reducers, valves, changes in pipe material and dead ends where necessary.

In-line valves, especially those DN 100 or larger, should be anchored to ensure stability under operational conditions. Refer to the NEDS drawing set, document number WS-02.

### Thrust blocks

#### General

The design of thrust blocks shall be based on the maximum test pressure and be considered at all tees, bends, dead ends and reducers. Generally fully welded PE pipes and fittings do not require thrust blocks on change of direction.

Thrust blocks shall be designed to resist the total unbalanced thrust and transmit all loads to the adjacent ground. Calculation of the unbalanced thrust shall be based on the maximum test pressure, or as otherwise specified by the WSE.

Restraint joint systems, specifically designed to resist the total unbalanced thrust, and support all thrust load, may be used for watermains up to 250 mm DN, instead of thrust blocks. These may include approved mechanical restraint coupling joints, or integral restraint seal systems. Manufacturers recommendations should be followed on any restraint system.

Where restraint joint systems are used thrust blocks shall be installed to isolate forces at any connection to pipework with un-restrained joints such as when making connections to AC, PVC and CI pipelines.

Typical contact areas for selected soil conditions and pipe sizes are shown in the NEDS drawing set, WS-12 to 14.

Thrust blocks for temporary infrastructure shall be designed to the requirements for permanent thrust blocks.

The designer should consider the suitable location of mechanical joints for maintenance, access, and inspection. Under some scenarios mechanical fittings are often not appropriate and may be declined by the WSE. Inappropriate scenarios include, but are not limited to, the use of non-restrained couplings or dismantling joints on PE pipes or use of fittings for purposes other than that which they are designed of e.g. use of a universal coupling as an articulation joint

### Anchor blocks

Anchor blocks are designed to prevent movement of pipe bends in a vertical direction. They consist of sufficient mass concrete to prevent pipe movement.

### Restrained elastomeric seal joint water mains

No information available in existing NZ codes.  Refer to AS 1646.1

### Restraint requirements for special situations

Commercially available mechanically restrained jointing systems may be used to avoid the need for thrust and anchor blocks subject to the approval of the WSE. However in some situations the WSE may still require the use of thrust and anchor blocks. The use of certain mechanical joint for ordinary pipe joints are prohibited, see advice Section 7.9.2.1. Refer to the WSE’s material supply standards for acceptable products.

#### Above-ground mains with unrestrained flexible joints

Water mains laid above-ground with flexible joints shall be provided with anchorage capable of restraining the main from movement at any point.

#### Buried steel mains with welded joints

Buried steel mains with continuous welded joints shall be considered self restraining.

#### Above-ground steel mains with welded joints

In such rarely approved situations restraint shall be provided against temperature induced movement as well as hydrostatic forces and other self and imposed loads.

#### Ductile iron and steel mains with flanged joints

Ductile iron and steel water mains with each and every joint flanged shall be considered to be self-anchoring.

#### PE mains

PE mains are generally prone to shrinkage and creep which occurs in trenchless methods of construction, and in open trenching.

The ends of PE mains shall be restrained with concrete thrust restraints. Where puddle flanges are to be used, suitable electrofusion fittings may be attached at each end of the pipeline as an alternative. Puddle flanges shall not be extrusion welded onto the PE pipe.

## BULKHEADS AND TRENCHSTOPS

#### Bulkheads for pipes on steep grades

Generally pipelines shall not be laid traversing steep grades, however when unavoidable, bulkheads, or anti-scour blocks, shall be detailed on the design drawings and shall be in accordance with Appendix A drawing WS-15. Spacing of bulkheads shall be as determined by Table 7-1.

| Table 7-1 – Spacing of bulkheads for pipes on steep grades |  |  |
| --- | --- | --- |
| Grade (%) | Requirement | Spacing (S) (m) |
| 15-35 | Concrete bulkhead | S = 100/Grade (%) |
| >35 | Special design | Refer to WSE |
| Note: On grades flatter than above where scour is a problem, sandbags may be used to stabilize the trench backfill. |  |  |

## UNFORESEEN GROUND CONDITIONS

In the event of unforeseen ground conditions being encountered during construction, the structural design shall be reviewed and appropriate amendments made to the Design Drawings.  Any changes shall be notified to the Entity and agreed in writing with the Entity prior to the continuation of construction.

## SEISMIC DESIGN

All pipes and structures shall be designed with adequate flexibility and special provisions to minimise risk of damage during earthquake. Historical experience in New Zealand earthquake events suggests that suitable pipe options, in seismically active areas, may include rubber ring joint PVC pipes PE pipes, ductile iron or steel pipe. Specially designed flexible joints shall be provided at all junctions between pipes and rigid structures (such as reservoirs, pump stations, bridges, and buildings) where pipe flexibility alone is not adequate to accommodate movement. Where structures are closely spaced such as at pump stations (not in the scope of this NEDS), base isolation of the area may be considered where minor actions are expected. Connecting to the base isolation area requires a flexible connection.

Guidance for pipe seismic design method and philosophy can found in “Seismic Guidelines for Water Pipelines”, American Lifelines Alliance, 2005, or “Guidelines for Seismic Design of Buried Pipelines”, NICEE, 2007, or Underground Utilities – Seismic assessment and design guidelines, Water NZ or, for PE pipelines, Seismic Design Guidelines are in AS/NZS 2033:2023 Appendix B General

Seismic resilience shall be considered for all new and upgraded infrastructure.  This includes pipelines, structures, pump stations and any associated fixtures and fittings.  Where the infrastructure consists of a number of connected structures (e.g. a pump station with detached valve chamber) each building and structure shall be given individual seismic assessment and design or the entire area shall be base isolated. 
Seismic designs shall ensure the provision of adequate flexibility and special provisions to minimise risk of damage during earthquakes. 
Seismic resilience and design shall consider direct damage to assets from shaking as well as damage caused by settlement, liquefaction or lateral spread of the ground supporting or surrounding the asset.  Seismic design shall consider:

- Magnitude of the design earthquake

Ground condition

Proximity to faults

Required level of resilience

Design of seismically resilient solutions shall follow either the Waka Kotahi NZ Transport Agency Bridge Manual or AS/NZS 1170:2004 – Structural Design Actions, whichever is most appropriate for the asset type and situation.  For some asset types the following are also relevant:

- Supporting NZS 3106:2009 – Design of Concrete Structures for the Storage of Liquids

NZ Building Code

NZS 4219:2009 – Seismic Performance of Engineering Systems in Buildings

Following the NZ Building Code November 2019 updates, local and regional authorities must prepare liquefaction hazard and hazard management maps.  These maps classify liquefaction by the likelihood and severity of damage and the uncertainty/precision of the classification.

The following documents provide additional information and guidance for pipe seismic design method and philosophy.  Where conflicts exist between this NEDS and these supporting documents this NEDS shall take precedence.

- Opus International Consultants.  “Underground Utilities – Seismic assessment and design guidelines”.  Water NZ.  2017.

https://www.waternz.org.nz/Resources/Article?Action=View&Article_id=1206·

Eidinger, J.  Maison, B.  Cheng, L.  Collins, F.  Conner, M.  Davis, C.  Matson, M.  O’Rouke, T.  Tang, A.  Wesling, J.  “Seismic Guidelines for Water Pipelines”.  American Lifelines Alliance.  2005.

https://www.americanlifelinesalliance.com/pdf/SeismicGuidelines_WaterPipelines_P1.pdf

Indian Institute of Technology Kanpur.  “IITK-GSDMA Guidelines for Seismic Design of Buried Pipelines”.  National Information Center of Earthquake Engineering.  2007.

http://www.iitk.ac.in/nicee/IITK-GSDMA/EQ28.pdf

### Buried Linear Assets

Buried linear assets are underground pipelines and associated fixtures including, but not limited to, valves, hydrants, sumps, anchor blocks and thrust blocks.

Seismic resilience of buried linear assets focusses on the ability to resist liquefaction, lateral spread or settlement.  Seismic resilient designs shall aim to:

- For pressure pipelines, remain in full operation without significant deformation or leakage

Seismic resilient design shall be completed for buried linear assets constructed in areas where:

- Liquefaction category is undetermined

Liquefaction damage is possible

High liquefaction vulnerability

Medium liquefaction vulnerability if the pipe serves 500 or more people, a facility for vulnerable people (e.g. a rest home) or a facility of significance to the community (e.g. a hospital).

Seismic resilience of pressure pipelines may be achieved by:

- Selecting ductile iron pipe with seismically resilient restrained joints (joints meeting ISO 16134 class S-1 for expansion/contraction, class A for pull-out resistance and a minimum joint deflection of 3 degrees)

Selecting polyethylene pipes with welded joints

Selecting PVC flexibly jointed pipes

consider jointing mechanism such as socket length and use of double rubber gaskets

### Above Ground and Non-Linear Structures

Above ground and point structures may be linear (e.g. an above ground pipeline or a pipeline attached to a bridge), non-linear buried structures (e.g. pump station wet well) or non-linear above ground structures (water supply pump stations).  Seismically resilient design of these structures shall consider both the effects of the shaking/ground acceleration and damage arising from liquefaction, lateral spread or settlement. 
Design of seismically resilient solutions shall use the standards, Codes and design guides covered in Section 7.12.1. 
Importance levels of structures shall comply with AS/NZS 1170.0 tables 3.1 and 3.2.  Apart from minor ancillary buildings at larger three waters facilities, above ground and non-linear structures will be IL3 or IL4. 
Seismic resilient design for resilience against ground acceleration shall be completed for all above ground and non-linear structures. 
Seismic resilient design for resilience against liquefaction, lateral spread or settlement shall be completed for above ground and non-linear structures constructed in areas where:

- Liquefaction category is undetermined

Liquefaction damage is possible

High liquefaction vulnerability

Medium liquefaction vulnerability

Seismically resilient designs shall aim to ensure:

- No damage limiting impacting the ability of a structure to provide the intended use and service life following an earthquake with a return period set by the serviceability limit state level 1 (SLS1).

Minor damage requiring repairs for the structure to provide the intended service life but no impact on use of the structure following an earthquake with a return period set by the serviceability limit state level 2 (SLS2).  For a reservoir this shall be defined as the reservoir (inclusive of the roof) retaining its contents with no leakage following a SLS2 return period event.

The structure can be expected to have lost structural integrity, become unstable or lost equilibrium while retaining a small residual load bearing capacity that prevents local or global collapse following an earthquake with a return period set by the ultimate limit state (ULS).  For a reservoir ULS shall be defined as the reservoir (inclusive of the roof) suffering limited cracking and leakage with no collapse or serious impact on the structure’s stability following a ULS return period event.

SLS1, SLS2 and ULS return periods shall depend on network and importance level as per Table 7-2 below.

| Table 7-2 – Network and importance level |  |  |  |  |
| --- | --- | --- | --- | --- |
| Network | Importance Level of Structure | SLS1 | SLS2 | ULS |
| Water Supply | IL4 | 1/25 | 1/1000 | 1/2500 |
|  | IL3 | 1/25 |  | 1/2500 |
|  | IL2 | 1/25 |  | 1/500 |
| Wastewater or Stormwater | IL4 | 1/25 | 1/500 | 1/2500 |
|  | IL3 | 1/25 |  | 1/2500 |
|  | IL2 | 1/25 |  | 1/500 |

### Connections Between Structures and Buried Assets

Specially designed flexible joints shall be provided at all junctions between pipes and rigid structures (such as reservoirs, pump stations, bridges, and buildings) irrespective of ground conditions. 
Flexible joint design depends on liquefaction vulnerability and criticality.  Some acceptable connection solutions are provided in the Table 7-3 below, however other solutions may be accepted by the WSE if the designer can prove they achieve the required outcome:

| Table 7-3 – Acceptable connection solutions |  |  |
| --- | --- | --- |
| Criticality | Undetermined Liquefaction Category AREAS, LIQUEFACTION Damage Possible Areas, Medium or High Liquefaction Vulnerability Areas | Very Low or Low Liquefaction Vulnerability Areas |
| Failure will affect 500 or more people, vulnerable facilities (e.g. a rest home) or significant facilities (e.g. a hospital) | Specialist design or flanged flexible joints designed for seismic resilience Cost-benefit analysis and Three Waters Entity approval required. | Self-restrained articulated joints |
| Failure affects less than 500 people and no vulnerable or significant facilities | Rocker pipe assemblies with addition of a fuse joint (an easily repairable weak spot in the system, designed to be the point of failure). Three Waters Entity approval required. | Rocker pipe |

# DESIGN REVIEW AND APPROVAL

## STAGE 2 ENGINEERING PLAN APPROVAL

Water infrastructure, including all private connections, require approval from the WSE, Council and where any of the work falls within state highway road reserve, also requires prior approval of NZTA.

For those water connections and developments requiring Stage 2 approval under the WSE’s Development Code a submission must be made to the WSE according to the details herein.

The NEDS set a level of design for particular types of infrastructure based on operational area and associated risk. The design standards provide the minimum criteria for establishing baseline standard design drawings, interface design between standardised components, establishing the correct sizing of components to complement the baseline parameters of standard drawings and the basis for developing bespoke designs. This document falls within the design standards category and must be read with the relevant drawings and standards for asset capture, materials supply and construction.

## DESIGN REVIEW

Once the detailed design has been completed, the Designer shall undertake a review to ensure the design complies with the requirements specified by the WSE in the Concept Plan, the concept design (refer to clause 1.2.2 Stage 1 Concept Plan Approval) and the requirements detailed in this NEDS. Compliance shall cover at least the following:

- Community impact adequately addressed

System components and configuration meet the Entity’s occupational health and safety requirements

Size(s) and grades of water mains throughout the portion of the proposed reticulation system meet Concept Plan requirements

Pipe materials are suitable for the particular application and environment

Water main layout and alignment meet WSE requirements

Route selection meets Concept Plan requirements

Topographical and environmental aspects have been addressed

Easements as appropriate are specified

Trenching and other geotechnical aspects have been considered

Provision is made for future extensions, as appropriate

Types and locations of control valves and any other necessary valves meet WSE requirements

Life cycle costs are minimized

Any departures or changes from the concept plan are highlighted and justified

## Documentation

### Reports

Unless otherwise directed by the WSE, the Designer shall provide the following documents upon completion of design:

- Safety in Design Report—details of risk assessment and outcomes used to justify the adopted item configuration.

Design drawings and specifications as detailed below.

Draft Operation and Maintenance Manuals—Operations and maintenance manuals in accordance with the WSE’s requirements.

Design Report—a copy of all calculations, clearly set out and complete with assumptions and references. If requested by the Water Entity at any time before or upon completion of design.

Approvals and Conditions—any copies of approvals and conditions from the local and regional authority including all resource consents, building consents, landowner consents and utilities and roading authority approvals.

Draft new asset register meeting the WSE’s requirements

The design shall be signed-off by a suitably qualified Chartered Professional Engineer, who may be required to additionally provide a signed Compliance statement if required by the WSE.

### Design Drawings

Design Drawings shall be prepared in accordance with the WSE’s requirements. Except where otherwise notified, the requirements are as set out in this Section.

Drawings shall be numbered in accordance with the WSE’s requirements.

The information to be shown in the Design Drawings shall include, but not be limited to, that detailed below. The information includes that required for production of As-Built drawings by facilitating, as far as possible, the ready incorporation or updating of such information in the Design Drawings.

Design Drawings generally shall include at least the following:

- A locality plan giving overall layout and location of the works and any access route

- Layout of roads, easements and lots

A detailed plan of the site showing all associated structures with all known buried and above-ground services and property/site information

- Layout plan/s of the works detailing :

  - Horizontal alignment of all proposed pipelines, hydrants and valves

  - Pipe material and type (including material, pressure and joint type as necessary)

  - Pipe Diameter, Level and grade

  - Chainages and offset distances from kerb line

  - Location of all building sites to be provided with fire protection

  - Position of all property connections relative to property boundaries and the depth at the property boundary

  - Notes specifying that detectable tape is to be laid on top of the pipe embedment or 1 m below the surface for all wastewater systems and pressure mains

  - Location of nearby utility services and stormwater drains

  - Major features (e.g., creeks, railway lines, power transmission lines)

  - Valve details – location, type, size

  - Thrust and Anchor block details

  - Lengths of pressure main between valves

Long sections of any pipelines 250mm NB and larger showing existing and proposed pipelines, cables and ducts crossing the alignment

Additional geological, construction and safety requirements

Geotechnical data, special foundation conditions, dewatering requirements

Pipe trench and embedment details

Pipe bridge details

Any particular corrosion protection requirements

Hydrostatic test pressure; and

A reinstatement plan and detail of the work area

Any special details and other information required by the WSE.

### Specifications

Specifications for a project shall be established by the Designer to define the precise standards of performance to achieve the project objectives, including:

- Precise standards of performance for construction work, products and materials, equipment and other items

Linkage between the project detailed design, the construction requirements, approved products and materials and adopted standard drawings of the WSE.

Specifications make it possible to express expected values when work or items are purchased or contracted for, and they provide means of determining conformance with expectations after purchase or construction.

Standard Specifications may be available from the Entity on request but shall be accompanied by particular specifications detailed project specific requirements.

## RECORDING OF AS BUILT INFORMATION

Asset information shall be progressively captured and supplied in accordance with the requirements of The WSE’s data and asset information standards and section 24 of this NEDS and the Entity’s Development Code.

NOT USED

PART TWO – CONSTRUCTION

| Appendices |  |  |
| --- | --- | --- |
| Appendices No. | Description |  |
| Appendix A | Water Standard Drawings |  |
|  | Drwg No | Drawing Title |
|  | WS-01 | Water Supply Customer Connection Layouts |
|  | WS-02 | Water Supply Intersection Layout |
|  | WS-03 | Water Supply Looped and Linked Main |
|  | WS-04 | Water Supply Valve and Hydrant Markings |
|  | WS-05 | Water Supply Valve Marker Post |
|  | WS-06 | Water Supply Hydrant Detail on New Main Flanged Tee |
|  | WS-07 | Water Supply Hydrant Detail on Existing Main Socketed Tee |
|  | WS-08 | Water Supply Sluice Valve ≥ DN80 |
|  | WS-09 | Water Supply Gate Valve ≤ DN50 |
|  | WS-10 | Water Supply Trench Re-Instatement Details |
|  | WS-11 | Water Supply Trench Bedding – Soft Ground |
|  | WS-12 | Water Supply Thruct Block – Bend/Elbow |
|  | WS-13 | Water Supply Thrust Block - Tees |
|  | WS-14 | Water Supply Thrust Block – Inline/Taper |
|  | WS-15 | Water Supply Pipeline Waterstop |
|  | WS-16 | Water Supply EF Tapping Saddle Connection |
|  | WS-17 | Water Supply Commercial Meter and Backflow Connection DN25-DN40 |
|  | WS-18 | Water Supply DN20 Metered and Unmetered Service Connection |
|  | WS-19 | Water Supply Customer Connection Restricted Supply |
|  | WS-20 | Water Supply Fire Suppression Supply and Separate Water Supply ≤ DN50 |
| Appendix B | Water Design Guide Matrix |  |
| Appendix C | Safety in Design Risk Register |  |
| Appendix D | Omissions & Opportunities Register |  |
| Appendix E | Concrete construction checklist |  |
| Appendix F | General Requirements for Site Butt Fusion Jointing |  |
| Appendix G | Electrofusion Welding Check Sheet |  |
| Appendix H | Compliance Requirement Check Sheet |  |
| Appendix I | Pipe Butt Weld Record Log Sheet |  |
| Appendix J | Pipe Electrofusion Weld Record Log Sheet |  |
| Appendix K | PE Weld testing Information Requirements |  |

Appendix A - Water Standard Drawings

Reference 1.2.3 for status of these drawings.

Appendix H - Compliance Requirement Check Sheet

Appendix I - Pipe Butt Weld Record Log Sheet

Appendix J - Pipe Electrofusion Weld Record Log Sheet

Appendix K - PE Weld testing Information Requirements